## Map
Quantity/Functionality | Details 1 | Details 2 | Resolution | Data Type | Access | Register (s) | Reg (Dec) | Nr of quantities | Size | Nr of registers | Base register (Hex) | Product Type | Functional Block | Ekip/Epic Integration
Active imp | kWh |  | 0.01 | Unsigned | Read | 5000 | 20480 | 1 | 4 | 4 | 5000 | M1M 15/20/30 | Data Reading - Energy (total) | Yes
Active exp | kWh |  | 0.01 | Unsigned | Read | 5004 | 20484 | 1 | 4 | 4 |  | M1M 20/30 | Data Reading - Energy (total) | Yes
Reactive imp | kvarh |  | 0.01 | Unsigned | Read | 500C | 20492 | 1 | 4 | 4 |  | M1M 15/20/30 | Data Reading - Energy (total) | Yes
Reactive exp | kvarh |  | 0.01 | Unsigned | Read | 5010 | 20496 | 1 | 4 | 4 |  | M1M 20/30 | Data Reading - Energy (total) | Yes
Apparent imp | kVA |  | 0.01 | Unsigned | Read | 5018 | 20504 | 1 | 4 | 4 |  | M1M 15/20/30 | Data Reading - Energy (total) | Yes
Three phase system | Line voltage | V | 0.1 | Unsigned | Read | 5B00 | 23296 | 1 | 2 | 2 | 5B00 | M1M 15/20/30 | Data Reading - Real-Time values | Yes
Phase Voltage L1 |  | V | 0.1 | Unsigned | Read | 5B02 | 23298 | 3 | 2 | 2 |  | M1M 15/20/30 | Data Reading - Real-Time values | Yes
Phase Voltage L2 |  | V | 0.1 | Unsigned | Read | 5B04 | 23300 | 3 | 2 | 2 |  | M1M 15/20/30 | Data Reading - Real-Time values | Yes
Phase Voltage L3 |  | V | 0.1 | Unsigned | Read | 5B06 | 23302 | 3 | 2 | 2 |  | M1M 15/20/30 | Data Reading - Real-Time values | Yes
Line voltage L1-L2 |  | V | 0.1 | Unsigned | Read | 5B08 | 23304 | 1 | 2 | 2 |  | M1M 15/20/30 | Data Reading - Real-Time values | Yes
Line voltage L3-L2 |  | V | 0.1 | Unsigned | Read | 5B0A | 23306 | 1 | 2 | 2 |  | M1M 15/20/30 | Data Reading - Real-Time values | Yes
Line voltage L1-L3 |  | V | 0.1 | Unsigned | Read | 5B0C | 23308 | 1 | 2 | 2 |  | M1M 15/20/30 | Data Reading - Real-Time values | Yes
Three phase Current |  | A | 0.01 | Unsigned | Read | 5B0E | 23310 | 1 | 2 | 2 |  | M1M 15/20/30 | Data Reading - Real-Time values | Yes
Current L1 |  |  | 0.01 | Unsigned | Read | 5B10 | 23312 | 4 | 2 | 2 |  | M1M 15/20/30 | Data Reading - Real-Time values | Yes
Current L2 |  |  | 0.01 | Unsigned | Read | 5B12 | 23314 | 4 | 2 | 2 |  | M1M 15/20/30 | Data Reading - Real-Time values | Yes
Current L3 |  |  | 0.01 | Unsigned | Read | 5B14 | 23316 | 4 | 2 | 2 |  | M1M 15/20/30 | Data Reading - Real-Time values | Yes
Current N |  |  | 0.01 | Unsigned | Read | 5B16 | 23318 | 4 | 2 | 2 |  | M1M 20/30 | Data Reading - Real-Time values | Yes
Active Power total |  |  | 0.01 | Signed | Read | 5B1A | 23322 | 4 | 2 | 2 |  | M1M 15/20/30 | Data Reading - Real-Time values | Yes
Active Power L1 |  |  | 0.01 | Signed | Read | 5B1C | 23324 | 4 | 2 | 2 |  | M1M 15/20/30 | Data Reading - Real-Time values | Yes
Active Power L2 |  |  | 0.01 | Signed | Read | 5B1E | 23326 | 4 | 2 | 2 |  | M1M 15/20/30 | Data Reading - Real-Time values | Yes
Active power L3 |  |  | 0.01 | Signed | Read | 5B20 | 23328 | 4 | 2 | 2 |  | M1M 15/20/30 | Data Reading - Real-Time values | Yes
Reactive Power total |  |  | 0.01 | Signed | Read | 5B22 | 23330 | 4 | 2 | 2 |  | M1M 15/20/30 | Data Reading - Real-Time values | Yes
Reactive Power L1 |  |  | 0.01 | Signed | Read | 5B24 | 23332 | 4 | 2 | 2 |  | M1M 15/20/30 | Data Reading - Real-Time values | Yes
Reactive Power L2 |  |  | 0.01 | Signed | Read | 5B26 | 23334 | 4 | 2 | 2 |  | M1M 15/20/30 | Data Reading - Real-Time values | Yes
Reactive Power L3 |  |  | 0.01 | Signed | Read | 5B28 | 23336 | 4 | 2 | 2 |  | M1M 15/20/30 | Data Reading - Real-Time values | Yes
Apparent Power total |  |  | 0.01 | Signed | Read | 5B2A | 23338 | 4 | 2 | 2 |  | M1M 15/20/30 | Data Reading - Real-Time values | Yes
Apparent Power L1 |  |  | 0.01 | Signed | Read | 5B2C | 23340 | 4 | 2 | 2 |  | M1M 15/20/30 | Data Reading - Real-Time values | Yes
Apparent Power L2 |  |  | 0.01 | Signed | Read | 5B2E | 23342 | 4 | 2 | 2 |  | M1M 15/20/30 | Data Reading - Real-Time values | Yes
Apaprent power L3 |  |  | 0.01 | Signed | Read | 5B30 | 23344 | 4 | 2 | 2 |  | M1M 15/20/30 | Data Reading - Real-Time values | Yes
Frequency |  |  | 0.01 | Unsigned | Read | 5B32 | 23346 | 1 | 1 | 1 |  | M1M 15/20/30 | Data Reading - Real-Time values | Yes
Phase angles | Power | Total, L1..L3 | 0.1 | Signed | Read | 5B33 | 23347 | 4 | 1 | 4 |  | M1M 15/20/30 | Data Reading - Real-Time values | Yes
| Voltage | L1..L3 | 0.1 | Signed | Read | 5B37 | 23351 | 3 | 1 | 3 |  | M1M 15/20/30 | Data Reading - Real-Time values | Yes
| Current | L1..L3 | 0.1 | Signed | Read | 5B3D | 23357 | 3 | 1 | 3 |  | M1M 15/20/30 | Data Reading - Real-Time values | Yes
Power factor total |  |  | 0.001 | Signed | Read | 5B40 | 23360 | 4 | 1 | 1 |  | M1M 15/20/30 | Data Reading - Real-Time values | Yes
Power factor L1 |  |  | 0.001 | Signed | Read | 5B41 | 23361 | 4 | 1 | 1 |  | M1M 15/20/30 | Data Reading - Real-Time values | Yes
Power factor L2 |  |  | 0.001 | Signed | Read | 5B42 | 23362 | 4 | 1 | 1 |  | M1M 15/20/30 | Data Reading - Real-Time values | Yes
Power factor L3 |  |  | 0.001 | Signed | Read | 5B43 | 23363 | 4 | 1 | 1 |  | M1M 15/20/30 | Data Reading - Real-Time values | Yes
Current quadrant |  |  | 1 | Unsigned | Read | 5B44 | 23364 | 4 | 1 | 1 |  | M1M 15/20/30 | Data Reading - Real-Time values | Yes
Displacement factor total | Cos phi |  | 0.001 | Signed | Read | 5B48 | 23368 | 4 | 1 | 1 |  | M1M 15/20/30 | Data Reading - Real-Time values
Displacement factor L1 | Cos phi |  | 0.001 | Signed | Read | 5B49 | 23369 | 4 | 1 | 1 |  | M1M 15/20/30 | Data Reading - Real-Time values
Displacement factor L2 | Cos phi |  | 0.001 | Signed | Read | 5B4A | 23370 | 4 | 1 | 1 |  | M1M 15/20/30 | Data Reading - Real-Time values
Displacement factor L3 | Cos phi |  | 0.001 | Signed | Read | 5B5B | 23387 | 4 | 1 | 1 |  | M1M 15/20/30 | Data Reading - Real-Time values
Average current L1 | A | Data value | 0.01 | Unsigned | Read | 5BD4 | 23508 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Average current L2 | A | Data value | 0.01 | Unsigned | Read | 5BD6 | 23510 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Average current L3 | A | Data value | 0.01 | Unsigned | Read | 5BD8 | 23512 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Average current neutral | A | Data value | 0.01 | Unsigned | Read | 5BDA | 23514 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Average voltage L1 | V | Data value | 0.1 | Unsigned | Read | 5BDC | 23516 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Average voltage L2 | V | Data value | 0.1 | Unsigned | Read | 5BDE | 23518 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Average voltage L3 | V | Data value | 0.1 | Unsigned | Read | 5BE0 | 23520 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Average voltage L1-L2 | V | Data value | 0.1 | Unsigned | Read | 5BE2 | 23522 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Average voltage L2-L3 | V | Data value | 0.1 | Unsigned | Read | 5BE4 | 23524 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Average voltage L1-L3 | V | Data value | 0.1 | Unsigned | Read | 5BE6 | 23526 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Average active power total | W | Data value | 0.01 | Signed | Read | 5BE8 | 23528 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Average active power L1 | W | Data value | 0.01 | Signed | Read | 5BEA | 23530 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Average active power L2 | W | Data value | 0.01 | Signed | Read | 5BEC | 23532 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Average active power L3 | W | Data value | 0.01 | Signed | Read | 5BEE | 23534 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Average reactive power total | var | Data value | 0.01 | Signed | Read | 5BF0 | 23536 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Average reactive power L1 | var | Data value | 0.01 | Signed | Read | 5BF2 | 23538 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Average reactive power L2 | var | Data value | 0.01 | Signed | Read | 5BF4 | 23540 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Average reactive power L3 | var | Data value | 0.01 | Signed | Read | 5BF6 | 23542 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Average apparent power total | VA | Data value | 0.01 | Signed | Read | 5BF8 | 23544 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Average apparent power L1 | VA | Data value | 0.01 | Signed | Read | 5BFA | 23546 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Average apparent power L2 | VA | Data value | 0.01 | Signed | Read | 5BFC | 23548 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Average apparent power L3 | VA | Data value | 0.01 | Signed | Read | 5BFE | 23550 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum current L1 | A | Data value | 0.01 | Unsigned | Read | 5C10 | 23568 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum current L2 | A | Data value | 0.01 | Unsigned | Read | 5C12 | 23570 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum current L3 | A | Data value | 0.01 | Unsigned | Read | 5C14 | 23572 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum current neutral | A | Data value | 0.01 | Unsigned | Read | 5C16 | 23574 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum voltage L1 | V | Data value | 0.1 | Unsigned | Read | 5C18 | 23576 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum voltage L2 | V | Data value | 0.1 | Unsigned | Read | 5C1A | 23578 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum voltage L3 | V | Data value | 0.1 | Unsigned | Read | 5C1C | 23580 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum voltage L1-L2 | V | Data value | 0.1 | Unsigned | Read | 5C1E | 23582 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum voltage L2-L3 | V | Data value | 0.1 | Unsigned | Read | 5C20 | 23584 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum voltage L1-L3 | V | Data value | 0.1 | Unsigned | Read | 5C22 | 23586 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum active power total | W | Data value | 0.01 | Signed | Read | 5C24 | 23588 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum active power L1 | W | Data value | 0.01 | Signed | Read | 5C26 | 23590 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum active power L2 | W | Data value | 0.01 | Signed | Read | 5C28 | 23592 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum active power L3 | W | Data value | 0.01 | Signed | Read | 5C2A | 23594 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum reactive power total | var | Data value | 0.01 | Signed | Read | 5C2C | 23596 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum reactive power L1 | var | Data value | 0.01 | Signed | Read | 5C2E | 23598 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum reactive power L2 | var | Data value | 0.01 | Signed | Read | 5C30 | 23600 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum reactive power L3 | var | Data value | 0.01 | Signed | Read | 5C32 | 23602 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum apparent power total | VA | Data value | 0.01 | Signed | Read | 5C34 | 23604 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum apparent power L1 | VA | Data value | 0.01 | Signed | Read | 5C36 | 23606 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum apparent power L2 | VA | Data value | 0.01 | Signed | Read | 5C38 | 23608 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum apparent power L3 | VA | Data value | 0.01 | Signed | Read | 5C3A | 23610 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum current L1 timestamp |  | Timestamp |  | Unsigned | Read | 5C4C | 23628 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum current L2 timestamp |  | Timestamp |  | Unsigned | Read | 5C4E | 23630 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum current L3 timestamp |  | Timestamp |  | Unsigned | Read | 5C50 | 23632 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum current neutral timestamp |  | Timestamp |  | Unsigned | Read | 5C52 | 23634 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum voltage L1 timestamp |  | Timestamp |  | Unsigned | Read | 5C54 | 23636 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum voltage L2 timestamp |  | Timestamp |  | Unsigned | Read | 5C56 | 23638 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum voltage L3 timestamp |  | Timestamp |  | Unsigned | Read | 5C58 | 23640 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum voltage L1-L2 timestamp |  | Timestamp |  | Unsigned | Read | 5C5A | 23642 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum voltage L2-L3 timestamp |  | Timestamp |  | Unsigned | Read | 5C5C | 23644 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum voltage L1-L3 timestamp |  | Timestamp |  | Unsigned | Read | 5C5E | 23646 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum active power total timestamp |  | Timestamp |  | Unsigned | Read | 5C60 | 23648 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum active power L1 timestamp |  | Timestamp |  | Unsigned | Read | 5C62 | 23650 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum active power L2 timestamp |  | Timestamp |  | Unsigned | Read | 5C64 | 23652 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum active power L3 timestamp |  | Timestamp |  | Unsigned | Read | 5C66 | 23654 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum reactive power total timestamp |  | Timestamp |  | Unsigned | Read | 5C68 | 23656 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum reactive power L1 timestamp |  | Timestamp |  | Unsigned | Read | 5C6A | 23658 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum reactive power L2 timestamp |  | Timestamp |  | Unsigned | Read | 5C6C | 23660 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum reactive power L3 timestamp |  | Timestamp |  | Unsigned | Read | 5C6E | 23662 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum apparent power total timestamp |  | Timestamp |  | Unsigned | Read | 5C70 | 23664 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum apparent power L1 timestamp |  | Timestamp |  | Unsigned | Read | 5C72 | 23666 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum apparent power L2 timestamp |  | Timestamp |  | Unsigned | Read | 5C74 | 23668 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Maximum apparent power L3 timestamp |  | Timestamp |  | Unsigned | Read | 5C76 | 23670 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum current L1 | A | Data value | 0.01 | Unsigned | Read | 5C88 | 23688 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum current L2 | A | Data value | 0.01 | Unsigned | Read | 5C8A | 23690 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum current L3 | A | Data value | 0.01 | Unsigned | Read | 5C8C | 23692 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum current neutral | A | Data value | 0.01 | Unsigned | Read | 5C8E | 23694 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum voltage L1 | V | Data value | 0.1 | Unsigned | Read | 5C90 | 23696 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum voltage L2 | V | Data value | 0.1 | Unsigned | Read | 5C92 | 23698 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum voltage L3 | V | Data value | 0.1 | Unsigned | Read | 5C94 | 23700 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum voltage L1-L2 | V | Data value | 0.1 | Unsigned | Read | 5C96 | 23702 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum voltage L2-L3 | V | Data value | 0.1 | Unsigned | Read | 5C98 | 23704 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum voltage L1-L3 | V | Data value | 0.1 | Unsigned | Read | 5C9A | 23706 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum active power total | W | Data value | 0.01 | Signed | Read | 5C9C | 23708 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum active power L1 | W | Data value | 0.01 | Signed | Read | 5C9E | 23710 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum active power L2 | W | Data value | 0.01 | Signed | Read | 5CA0 | 23712 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum active power L3 | W | Data value | 0.01 | Signed | Read | 5CA2 | 23714 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum reactive power total | var | Data value | 0.01 | Signed | Read | 5CA4 | 23716 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum reactive power L1 | var | Data value | 0.01 | Signed | Read | 5CA6 | 23718 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum reactive power L2 | var | Data value | 0.01 | Signed | Read | 5CA8 | 23720 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum reactive power L3 | var | Data value | 0.01 | Signed | Read | 5CAA | 23722 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum apparent power total | VA | Data value | 0.01 | Signed | Read | 5CAC | 23724 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum apparent power L1 | VA | Data value | 0.01 | Signed | Read | 5CAE | 23726 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum apparent power L2 | VA | Data value | 0.01 | Signed | Read | 5CB0 | 23728 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum apparent power L3 | VA | Data value | 0.01 | Signed | Read | 5CB2 | 23730 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum current L1 timestamp |  | Timestamp |  | Unsigned | Read | 5CC4 | 23748 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum current L2 timestamp |  | Timestamp |  | Unsigned | Read | 5CC6 | 23750 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum current L3 timestamp |  | Timestamp |  | Unsigned | Read | 5CC8 | 23752 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum current neutral timestamp |  | Timestamp |  | Unsigned | Read | 5CCA | 23754 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum voltage L1 timestamp |  | Timestamp |  | Unsigned | Read | 5CCC | 23756 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum voltage L2 timestamp |  | Timestamp |  | Unsigned | Read | 5CCE | 23758 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum voltage L3 timestamp |  | Timestamp |  | Unsigned | Read | 5CD0 | 23760 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum voltage L1-L2 timestamp |  | Timestamp |  | Unsigned | Read | 5CD2 | 23762 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum voltage L2-L3 timestamp |  | Timestamp |  | Unsigned | Read | 5CD4 | 23764 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum voltage L1-L3 timestamp |  | Timestamp |  | Unsigned | Read | 5CD6 | 23766 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum active power total timestamp |  | Timestamp |  | Unsigned | Read | 5CD8 | 23768 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum active power L1 timestamp |  | Timestamp |  | Unsigned | Read | 5CDA | 23770 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum active power L2 timestamp |  | Timestamp |  | Unsigned | Read | 5CDC | 23772 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum active power L3 timestamp |  | Timestamp |  | Unsigned | Read | 5CDE | 23774 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum reactive power total timestamp |  | Timestamp |  | Unsigned | Read | 5CE0 | 23776 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum reactive power L1 timestamp |  | Timestamp |  | Unsigned | Read | 5CE2 | 23778 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum reactive power L2 timestamp |  | Timestamp |  | Unsigned | Read | 5CE4 | 23780 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum reactive power L3 timestamp |  | Timestamp |  | Unsigned | Read | 5CE6 | 23782 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum apparent power total timestamp |  | Timestamp |  | Unsigned | Read | 5CE8 | 23784 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum apparent power L1 timestamp |  | Timestamp |  | Unsigned | Read | 5CEA | 23786 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum apparent power L2 timestamp |  | Timestamp |  | Unsigned | Read | 5CEC | 23788 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Minimum apparent power L3 timestamp |  | Timestamp |  | Unsigned | Read | 5CEE | 23790 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Voltage harmonics | L1 (THD) | % | 0.1 | Unsigned | Read | 5D00 | 23808 | 1 | 1 | 1 |  | M1M 30 | Data Reading - Power Quality | Yes
| L1 (2nd,3rd…40th) | % | 0.1 | Unsigned | Read | 5D01 | 23809 | 40 | 1 | 40 |  | M1M 30 | Data Reading - Power Quality
| L2 (THD) | % | 0.1 | Unsigned | Read | 5D80 | 23936 | 1 | 1 | 1 |  | M1M 30 | Data Reading - Power Quality | Yes
| L2 (2nd,3rd…40th) | % | 0.1 | Unsigned | Read | 5D81 | 23937 | 40 | 1 | 40 |  | M1M 30 | Data Reading - Power Quality
| L3 (THD) | % | 0.1 | Unsigned | Read | 5E00 | 24064 | 1 | 1 | 1 |  | M1M 30 | Data Reading - Power Quality | Yes
| L3 (2nd,3rd…40th) | % | 0.1 | Unsigned | Read | 5E01 | 24065 | 40 | 1 | 40 |  | M1M 30 | Data Reading - Power Quality
| L1-L2 (THD) | % | 0.1 | Unsigned | Read | 5E80 | 24192 | 1 | 1 | 1 |  | M1M 30 | Data Reading - Power Quality | Yes
| L1-L2 (2nd,3rd…40th) | % | 0.1 | Unsigned | Read | 5E81 | 24193 | 40 | 1 | 40 |  | M1M 30 | Data Reading - Power Quality
| L3-L2 (THD) | % | 0.1 | Unsigned | Read | 5F00 | 24320 | 1 | 1 | 1 |  | M1M 30 | Data Reading - Power Quality | Yes
| L3-L2 (2nd,3rd…40th) | % | 0.1 | Unsigned | Read | 5F01 | 24321 | 40 | 1 | 40 |  | M1M 30 | Data Reading - Power Quality
| L1-L3 (THD) | % | 0.1 | Unsigned | Read | 5F80 | 24448 | 1 | 1 | 1 |  | M1M 30 | Data Reading - Power Quality | Yes
| L1-L3 (2nd,3rd…40th) | % | 0.1 | Unsigned | Read | 5F81 | 24449 | 40 | 1 | 40 |  | M1M 30 | Data Reading - Power Quality
Current harmonics | L1 (THD) | % | 0.1 | Unsigned | Read | 6000 | 24576 | 1 | 1 | 1 |  | M1M 30 | Data Reading - Power Quality | Yes
| L1 (2nd,3rd…40th) | % | 0.1 | Unsigned | Read | 6001 | 24577 | 40 | 1 | 40 |  | M1M 30 | Data Reading - Power Quality
| L2 (THD) | % | 0.1 | Unsigned | Read | 6080 | 24704 | 1 | 1 | 1 |  | M1M 30 | Data Reading - Power Quality | Yes
| L2 (2nd,3rd…40th) | % | 0.1 | Unsigned | Read | 6081 | 24705 | 40 | 1 | 40 |  | M1M 30 | Data Reading - Power Quality
| L3 (THD) | % | 0.1 | Unsigned | Read | 6100 | 24832 | 1 | 1 | 1 |  | M1M 30 | Data Reading - Power Quality | Yes
| L3 (2nd,3rd…40th) | % | 0.1 | Unsigned | Read | 6101 | 24833 | 40 | 1 | 40 |  | M1M 30 | Data Reading - Power Quality
| N (THD) | % | 0.1 | Unsigned | Read | 6180 | 24960 | 1 | 1 | 1 |  | M1M 30 | Data Reading - Power Quality | Yes
| N (2nd,3rd…40th) | % | 0.1 | Unsigned | Read | 6181 | 24961 | 40 | 1 | 40 |  | M1M 30 | Data Reading - Power Quality
Unbalances | Phase voltage | % | 0.1 | Unsigned | Read | 6200 | 25088 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Power Quality | Yes
| Line voltage | % | 0.1 | Unsigned | Read | 6202 | 25090 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Power Quality | Yes
| Current | % | 0.1 | Unsigned | Read | 6204 | 25092 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Power Quality | Yes
Inputs | Input 1..8 | status of the I/O configured as input |  |  |  | 6308 | 25352 | 8 | 1 | 8 |  | M1M 20/30 | Data Reading - I/O | Yes
Counters | Input 1..8 | Counters for pulse inputs |  |  |  | 6318 | 25368 | 8 | 4 | 32 |  | M1M 20/30 | Data Reading - I/O | Yes
Serial number(s) |  |  |  | ASCII | Read | 8900 | 35072 | 1 | 5 | 5 | 8900 | M1M 15/20/30 | Configuration - Device info | Yes
Meter firmware version |  |  |  | ASCII | Read | 8908 | 35080 | 1 | 8 | 8 |  | M1M 15/20/30 | Configuration - Device info | Yes
Product type number ID | Sheet 2 |  |  |  |  | 8910 | 35088 | 1 | 1 | 1 |  | M1M 15/20/30 | Configuration - Device info | Yes
Product tag name |  |  |  |  | Read/Write | 8919 | 35097 | 1 | 5 | 5 |  | M1M 15/20/30 | Configuration - Device info | No
Type designation |  |  |  | ASCII | Read | 8960 | 35168 | 1 | 6 | 6 |  | M1M 15/20/30 | Configuration - Device info | No
Product Name | E.g. M1M 30 MODBUS |  |  | ASCII | Read | 8966 | 35174 | 1 | 8 | 8 |  | M1M 15/20/30 | Configuration - Device info | Yes
Date Time | YYMMDD:HHMMSS | Read/Write |  |  | Read/Write | 8A00 | 35328 | 1 | 3 | 3 | 8A00 | M1M 30 | Configuration - Date and Time | Yes
Transformer ratios | Current transf ratio (Numerator) |  |  | Unsigned | Read/Write | 8C00 | 35840 | 1 | 2 | 2 | 8C00 | M1M 15/20/30 | Configuration - Installation | Yes
| Current transf ratio (Denominator) |  |  | Unsigned | Read/Write | 8C02 | 35842 | 1 | 2 | 2 |  | M1M 15/20/30 | Configuration - Installation | Yes
| Voltage transf ratio (Numerator) |  |  | Unsigned | Read/Write | 8C04 | 35844 | 1 | 2 | 2 |  | M1M 15/20/30 | Configuration - Installation | Yes
| Voltage transf ratio (Denominator) |  |  | Unsigned | Read/Write | 8C06 | 35846 | 1 | 2 | 2 |  | M1M 15/20/30 | Configuration - Installation | Yes
Modbus RTU | Address | 1 - 247 |  | Unsigned | Read/Write | 8CEB | 36075 | 1 | 1 | 1 | 8CEB | M1M 15/20/30 | Configuration - Communication | Yes
| Baudrate | 9600, 19200, 38400, 57600, 115200 |  | Unsigned | Read/Write | 8CEC | 36076 | 1 | 2 | 2 |  | M1M 15/20/30 | Configuration - Communication | Yes
| Parity | 0- none; 1-even; 2- odd |  | Unsigned | Read/Write | 8CEE | 36078 | 1 | 1 | 1 |  | M1M 15/20/30 | Configuration - Communication | Yes
Ethernet | DHCP | 0-disable; 1- enable |  | Unsigned | Read/Write | 8CEF | 36079 | 1 | 1 | 1 | 8CEF | M1M 30 | Configuration - Communication | Yes
| IP | A.B.C.D -> 0xAABBCCDD |  | Unsigned | Read/Write | 8CF0 | 36080 | 1 | 2 | 2 |  | M1M 30 | Configuration - Communication | Yes
| Mask | A.B.C.D -> 0xAABBCCDD |  | Unsigned | Read/Write | 8CF2 | 36082 | 1 | 2 | 2 |  | M1M 30 | Configuration - Communication | Yes
| Gateway | A.B.C.D -> 0xAABBCCDD |  | Unsigned | Read/Write | 8CF4 | 36084 | 1 | 2 | 2 |  | M1M 30 | Configuration - Communication | Yes
Active power total Scaler 1 | W |  | 1 | Signed | Read | CB1A | 51994 | 1 | 2 | 2 | C000 | M1M 15/20/30 | Data Reading - Real-Time values
Active power L1 Scaler 1 | W |  | 1 | Signed | Read | CB1C | 51996 | 1 | 2 | 2 |  | M1M 15/20/30 | Data Reading - Real-Time values
Active power L2 Scaler 1 | W |  | 1 | Signed | Read | CB1E | 51998 | 1 | 2 | 2 |  | M1M 15/20/30 | Data Reading - Real-Time values
Active power L3 Scaler 1 | W |  | 1 | Signed | Read | CB20 | 52000 | 1 | 2 | 2 |  | M1M 15/20/30 | Data Reading - Real-Time values
Reactive power total Scaler 1 | VAR |  | 1 | Signed | Read | CB22 | 52002 | 1 | 2 | 2 |  | M1M 15/20/30 | Data Reading - Real-Time values
Reactive power L1 Scaler 1 | VAR |  | 1 | Signed | Read | CB24 | 52004 | 1 | 2 | 2 |  | M1M 15/20/30 | Data Reading - Real-Time values
Reactive power L2 Scaler 1 | VAR |  | 1 | Signed | Read | CB26 | 52006 | 1 | 2 | 2 |  | M1M 15/20/30 | Data Reading - Real-Time values
Reactive power L3 Scaler 1 | VAR |  | 1 | Signed | Read | CB28 | 52008 | 1 | 2 | 2 |  | M1M 15/20/30 | Data Reading - Real-Time values
Apparent power total Scaler 1 | VA |  | 1 | Signed | Read | CB2A | 52010 | 1 | 2 | 2 |  | M1M 15/20/30 | Data Reading - Real-Time values
Apparent power L1 Scaler 1 | VA |  | 1 | Signed | Read | CB2C | 52012 | 1 | 2 | 2 |  | M1M 15/20/30 | Data Reading - Real-Time values
Apparent power L2 Scaler 1 | VA |  | 1 | Signed | Read | CB2E | 52014 | 1 | 2 | 2 |  | M1M 15/20/30 | Data Reading - Real-Time values
Apparent power L3 Scaler 1 | VA |  | 1 | Signed | Read | CB30 | 52016 | 1 | 2 | 2 |  | M1M 15/20/30 | Data Reading - Real-Time values
Average Active power total Scaler 1 | W |  | 1 | Signed | Read | CBE8 | 52200 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Average Active power L1 Scaler 1 | W |  | 1 | Signed | Read | CBEA | 52202 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Average Active power L2 Scaler 1 | W |  | 1 | Signed | Read | CBEC | 52204 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Average Active power L3 Scaler 1 | W |  | 1 | Signed | Read | CBEE | 52206 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Average Reactive power total Scaler 1 | VAR |  | 1 | Signed | Read | CBF0 | 52208 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Average Reactive power L1 Scaler 1 | VAR |  | 1 | Signed | Read | CBF2 | 52210 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Average Reactive power L2 Scaler 1 | VAR |  | 1 | Signed | Read | CBF4 | 52212 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Average Reactive power L3 Scaler 1 | VAR |  | 1 | Signed | Read | CBF6 | 52214 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Average Apparent power total Scaler 1 | VA |  | 1 | Signed | Read | CBF8 | 52216 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Average Apparent power L1 Scaler 1 | VA |  | 1 | Signed | Read | CBFA | 52218 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Average Apparent power L2 Scaler 1 | VA |  | 1 | Signed | Read | CBFC | 52220 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Average Apparent power L3 Scaler 1 | VA |  | 1 | Signed | Read | CBFE | 52222 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Max Active power total Scaler 1 | W |  | 1 | Signed | Read | CC24 | 52260 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Max Active power L1 Scaler 1 | W |  | 1 | Signed | Read | CC26 | 52262 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Max Active power L2 Scaler 1 | W |  | 1 | Signed | Read | CC28 | 52264 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Max Active power L3 Scaler 1 | W |  | 1 | Signed | Read | CC2A | 52266 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Max Reactive power total Scaler 1 | VAR |  | 1 | Signed | Read | CC2C | 52268 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Max Reactive power L1 Scaler 1 | VAR |  | 1 | Signed | Read | CC2E | 52270 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Max Reactive power L2 Scaler 1 | VAR |  | 1 | Signed | Read | CC30 | 52272 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Max Reactive power L3 Scaler 1 | VAR |  | 1 | Signed | Read | CC32 | 52274 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Max Apparent power total Scaler 1 | VA |  | 1 | Signed | Read | CC34 | 52276 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Max Apparent power L1 Scaler 1 | VA |  | 1 | Signed | Read | CC36 | 52278 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Max Apparent power L2 Scaler 1 | VA |  | 1 | Signed | Read | CC38 | 52280 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Max Apparent power L3 Scaler 1 | VA |  | 1 | Signed | Read | CC3A | 52282 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Min Active power total Scaler 1 | W |  | 1 | Signed | Read | CC9C | 52380 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Min Active power L1 Scaler 1 | W |  | 1 | Signed | Read | CC9E | 52382 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Min Active power L2 Scaler 1 | W |  | 1 | Signed | Read | CCA0 | 52384 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Min Active power L3 Scaler 1 | W |  | 1 | Signed | Read | CCA2 | 52386 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Min Reactive power total Scaler 1 | VAR |  | 1 | Signed | Read | CCA4 | 52388 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Min Reactive power L1 Scaler 1 | VAR |  | 1 | Signed | Read | CCA6 | 52390 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Min Reactive power L2 Scaler 1 | VAR |  | 1 | Signed | Read | CCA8 | 52392 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Min Reactive power L3 Scaler 1 | VAR |  | 1 | Signed | Read | CCAA | 52394 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Min Apparent power total Scaler 1 | VA |  | 1 | Signed | Read | CCAC | 52396 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Min Apparent power L1 Scaler 1 | VA |  | 1 | Signed | Read | CCAE | 52398 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Min Apparent power L2 Scaler 1 | VA |  | 1 | Signed | Read | CCB0 | 52400 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values
Min Apparent power L3 Scaler 1 | VA |  | 1 | Signed | Read | CCB2 | 52402 | 1 | 2 | 2 |  | M1M 30 | Data Reading - Avg/Min/Max values

## Obis Codes
QUANTITY | OBIS Code
TOTAL ENERGIES:
Active energy import total | 1.0.1.8.0.255
Active energy export total | 1.0.2.8.0.255
Active energy net total | 1.0.16.8.0.255
Reactive energy import total | 1.0.3.8.0.255
Reactive energy export total | 1.0.4.8.0.255
Reactive energy net total | 1.0.128.8.0.255
Apparent energy import total | 1.0.9.8.0.255
Apparent energy export total | 1.0.10.8.0.255
Apparent energy net total | 1.0.137.8.0.255
Active energy import total CO2 | 1.0.1.8.200.255
Active energy import total Currency | 1.0.1.8.220.255
ENERGIES PER TARIFF:
Active energy import tariff 1 | 1.0.1.8.1.255
Active energy import tariff 2 | 1.0.1.8.2.255
Active energy import tariff 3 | 1.0.1.8.3.255
Active energy import tariff 4 | 1.0.1.8.4.255
Active energy import tariff 5 | 1.0.1.8.5.255
Active energy import tariff 6 | 1.0.1.8.6.255
Active energy export tariff 1 | 1.0.2.8.1.255
Active energy export tariff 2 | 1.0.2.8.2.255
Active energy export tariff 3 | 1.0.2.8.3.255
Active energy export tariff 4 | 1.0.2.8.4.255
Active energy export tariff 5 | 1.0.2.8.5.255
Active energy export tariff 6 | 1.0.2.8.6.255
Reactive energy import tariff 1 | 1.0.3.8.1.255
Reactive energy import tariff 2 | 1.0.3.8.2.255
Reactive energy import tariff 3 | 1.0.3.8.3.255
Reactive energy import tariff 4 | 1.0.3.8.4.255
Reactive energy import tariff 5 | 1.0.3.8.5.255
Reactive energy import tariff 6 | 1.0.3.8.6.255
Reactive energy export tariff 1 | 1.0.4.8.1.255
Reactive energy export tariff 2 | 1.0.4.8.2.255
Reactive energy export tariff 3 | 1.0.4.8.3.255
Reactive energy export tariff 4 | 1.0.4.8.4.255
Reactive energy export tariff 5 | 1.0.4.8.5.255
Reactive energy export tariff 6 | 1.0.4.8.6.255
ENERGIES PER PHASE:
Active energy import L1 | 1.0.21.8.0.255
Active energy import L2 | 1.0.41.8.0.255
Active energy import L3 | 1.0.61.8.0.255
Active energy export L1 | 1.0.22.8.0.255
Active energy export L2 | 1.0.42.8.0.255
Active energy export L3 | 1.0.62.8.0.255
Active energy net L1 | 1.0.36.8.0.255
Active energy net L2 | 1.0.56.8.0.255
Active energy net L3 | 1.0.76.8.0.255
Reactive energy import L1 | 1.0.23.8.0.255
Reactive energy import L2 | 1.0.43.8.0.255
Reactive energy import L3 | 1.0.63.8.0.255
Reactive energy export L1 | 1.0.24.8.0.255
Reactive energy export L2 | 1.0.44.8.0.255
Reactive energy export L3 | 1.0.64.8.0.255
Reactive energy net L1 | 1.0.129.8.0.255
Reactive energy net L2 | 1.0.130.8.0.255
Reactive energy net L3 | 1.0.131.8.0.255
Apparent energy import L1 | 1.0.29.8.0.255
Apparent energy import L2 | 1.0.49.8.0.255
Apparent energy import L3 | 1.0.69.8.0.255
Apparent energy export L1 | 1.0.30.8.0.255
Apparent energy export L2 | 1.0.50.8.0.255
Apparent energy export L3 | 1.0.70.8.0.255
Apparent energy net L1 | 1.0.138.8.0.255
Apparent energy net L2 | 1.0.139.8.0.255
Apparent energy net L3 | 1.0.140.8.0.255
INPUTS:
Input 1 counter | 1.128.82.8.0.255
Input 2 counter | 1.129.82.8.0.255
Input 3 counter | 1.130.82.8.0.255
Input 4 counter | 1.131.82.8.0.255
Input 5 counter | 1.132.82.8.0.255
Input 6 counter | 1.133.82.8.0.255
LOAD PROFILE: AVERAGE OF INSTRUMENTATION VALUE
Voltage L1 | 1.0.32.27.0.255
Voltage L2 | 1.0.52.27.0.255
Voltage L3 | 1.0.72.27.0.255
Voltage L1-L2 | 1.0.134.27.0.255
Voltage L2-L3 | 1.0.135.27.0.255
Voltage L1-L3 | 1.0.136.27.0.255
Current L1 | 1.0.31.27.0.255
Current L2 | 1.0.51.27.0.255
Current L3 | 1.0.71.27.0.255
Current N | 1.0.91.27.0.255
THD Voltage L1 | 1.0.32.27.124.255
THD Voltage L2 | 1.0.52.27.124.255
THD Voltage L3 | 1.0.72.27.124.255
THD Voltage L1-L2 | 1.0.134.27.124.255
THD Voltage L2-L3 | 1.0.135.27.124.255
THD Voltage L1-L3 | 1.0.136.27.124.255
THD Current L1 | 1.0.31.27.124.255
THD Current L2 | 1.0.51.27.124.255
THD Current L3 | 1.0.71.27.124.255
THD Current N | 1.0.91.27.124.255
Power factor total | 1.0.13.27.0.255
Power factor L1 | 1.0.33.27.0.255
Power factor L2 | 1.0.53.27.0.255
Power factor L3 | 1.0.73.27.0.255
Active power import total | 1.0.16.27.0.255
Active power import L1 | 1.0.36.27.0.255
Active power import L2 | 1.0.56.27.0.255
Active power import L3 | 1.0.76.27.0.255
Reactive power import total | 1.0.128.27.0.255
Reactive power import L1 | 1.0.129.27.0.255
Reactive power import L2 | 1.0.130.27.0.255
Reactive power import L3 | 1.0.131.27.0.255
Apparent power import total | 1.0.137.27.0.255
Apparent power import L1 | 1.0.138.27.0.255
Apparent power import L2 | 1.0.139.27.0.255
Apparent power import L3 | 1.0.140.27.0.255
Active power export total | 1.0.17.27.0.255
Active power export L1 | 1.0.37.27.0.255
Active power export L2 | 1.0.57.27.0.255
Active power export L3 | 1.0.77.27.0.255
Reactive power export total | 1.0.228.27.0.255
Reactive power export L1 | 1.0.229.27.0.255
Reactive power export L2 | 1.0.230.27.0.255
Reactive power export L3 | 1.0.231.27.0.255
Apparent power export total | 1.0.237.27.0.255
Apparent power export L1 | 1.0.238.27.0.255
Apparent power export L2 | 1.0.239.27.0.255
Apparent power export L3 | 1.0.240.27.0.255
DEMAND MIN/MAX OF INSTRUMENTATION VALUES AND POWERS |  | Value of X | Meaning
Voltage L1 | 1.0.32.X.0.255 | 3 | Minimum value of averages calculated over measurement period
Voltage L2 | 1.0.52.X.0.255 | 6 | Maximum value of averages calculated over measurement period
Voltage L3 | 1.0.72.X.0.255 | 13 | Minimum sliding value of averages calculated over measurement period
Voltage L1-L2 | 1.0.134.X.0.255 | 16 | Maximum sliding value of averages calculated over measurement period
Voltage L2-L3 | 1.0.135.X.0.255
Voltage L1-L3 | 1.0.136.X.0.255
Current L1 | 1.0.31.X.0.255
Current L2 | 1.0.51.X.0.255
Current L3 | 1.0.71.X.0.255
Current N | 1.0.91.X.0.255
THD Voltage L1 | 1.0.32.X.124.254
THD Voltage L2 | 1.0.52.X.124.254
THD Voltage L3 | 1.0.72.X.124.254
THD Voltage L1-L2 | 1.0.134.X.124.254
THD Voltage L2-L3 | 1.0.135.X.124.254
THD Voltage L1-L3 | 1.0.136.X.124.254
THD Current L1 | 1.0.31.X.124.254
THD Current L2 | 1.0.51.X.124.254
THD Current L3 | 1.0.71.X.124.254
THD Current N | 1.0.91.X.124.254
Power factor total | 1.0.13.X.0.255
Power factor L1 | 1.0.33.X.0.255
Power factor L2 | 1.0.53.X.0.255
Power factor L3 | 1.0.73.X.0.255
Powers | Same codes as energies, but with X set to 3, 6, 13 or 16
QUANTITY IDENTIFIERS MONITORED BY ALARMS:
Voltage L1 | 1.0.32.27.0.255
Voltage L2 | 1.0.52.27.0.255
Voltage L3 | 1.0.72.27.0.255
Voltage L1-L2 | 1.0.134.27.0.255
Voltage L2-L3 | 1.0.135.27.0.255
Voltage L1-L3 | 1.0.136.27.0.255
Current L1 | 1.0.31.27.0.255
Current L2 | 1.0.51.27.0.255
Current L3 | 1.0.71.27.0.255
Current N | 1.0.91.27.0.255
Active power total | 1.0.16. 7.0.255
Active power L1 | 1.0.36. 7.0.255
Active power L2 | 1.0.56. 7.0.255
Active power L3 | 1.0.76. 7.0.255
Rective power total | 1.0.128. 7.0.255
Rective power L1 | 1.0.129. 7.0.255
Rective power L2 | 1.0.130. 7.0.255
Rective power L3 | 1.0.131. 7.0.255
Apparent power total | 1.0.137. 7.0.255
Apparent power L1 | 1.0.138. 7.0.255
Apparent power L2 | 1.0.139. 7.0.255
Apparent power L3 | 1.0.140. 7.0.255
Power factor total | 1.0.13.7.0.255
Power factor L1 | 1.0.33.7.0.255
Power factor L2 | 1.0.53.7.0.255
Power factor L3 | 1.0.73.7.0.255
Harmonic voltage L1 | 1.0.32.7.124.255
Harmonic voltage L2 | 1.0.52.7.124.255
Harmonic voltage L3 | 1.0.72.7.124.255
Harmonic voltage L1-L2 | 1.0.134.7.124.255
Harmonic voltage L2-L3 | 1.0.135.7.124.255
Harmonic voltage L1-L3 | 1.0.136.7.124.255
Harmonic current L1 | 1.0.31.7.124.255
Harmonic current L2 | 1.0.51.7.124.255
Harmonic current L3 | 1.0.71.7.124.255
Harmonic current Neutral | 1.0.91.7.124.255

## Details
Product type number ID | DESCRIPTION
60 | M1M 15
61 | M1M 15 MODBUS RTU
62 | M1M 20
63 | M1M 20 MODBUS RTU
64 | M1M 20 Ethernet
65 | M1M 20 IO MODBUS RTU
66 | M1M 30 MODBUS RTU
67 | M1M 30 Ethernet
68 | M1M 30 IO MODBUS RTU
Wires
M4M 20 (all type Ids 0:6)
3Ph/4W/3CT = 1
3 phase-4 wires network+3CTs
3Ph/4W/1CT = 2
3 phase-4 wires network+1CTs
3Ph/3W/3CT = 3
3 phase-3 wires network+3CTs
3Ph/3W/2CT = 4
3 phase-3 wires network+2CTs
3Ph/3W/1CT = 5
3 phase-3 wires network+1CTs
2Ph/3W/2CT = 6
2 phase-3 wires network+2CTs
1Ph/2W/1CT = 7
1 phase-2 wires network+1CTs
M4M 30 (all type Ids 7:12)
3Ph/4W/4CT = 0
3 phase-4 wires network+4CTs
3Ph/4W/3CT = 1
3 phase-4 wires network+3CTs
3Ph/4W/1CT = 2
3 phase-4 wires network+1CTs
3Ph/3W/3CT = 3
3 phase-3 wires network+3CTs
3Ph/3W/2CT = 4
3 phase-3 wires network+2CTs
3Ph/3W/1CT = 5
3 phase-3 wires network+1CTs
2Ph/3W/2CT = 6
2 phase-3 wires network+2CTs
1Ph/2W/1CT = 7
1 phase-2 wires network+1CTs

## BR Legacy 1
Reg[Dec] | Reg[Hex] | Measurement description | Unit | Format
100 | 64 | Voltage L1 and Neutral | V | Signed integer 16 bits
101 | 65 | Voltage L2 and Neutral | V | Signed integer 16 bits
102 | 66 | Voltage L3 and Neutral | V | Signed integer 16 bits
103 | 67 | Voltage L1 and L2 | V | Signed integer 16 bits
104 | 68 | Voltage L2 and L3 | V | Signed integer 16 bits
105 | 69 | Voltage L3 and L1 | V | Signed integer 16 bits
106 | 6A | Current phase 1 | A | Signed integer 16 bits
107 | 6B | Current phase 2 | A | Signed integer 16 bits
108 | 6C | Current phase 3 | A | Signed integer 16 bits
109 | 6D | Neutral current | A | Signed integer 16 bits
110 | 6E | Active power phase 1 | W | Signed integer 16 bits
111 | 6F | Active power phase 2 | W | Signed integer 16 bits
112 | 70 | Active power phase 3 | W | Signed integer 16 bits
113 | 71 | Active power total | W | Signed integer 16 bits
114 | 72 | Reactive power phase 1 | var | Signed integer 16 bits
115 | 73 | Reactive power phase 2 | var | Signed integer 16 bits
116 | 74 | Reactive power phase 3 | var | Signed integer 16 bits
117 | 75 | Reactive power total | var | Signed integer 16 bits
118 | 76 | Apparente power fase 1 | VA | Signed integer 16 bits
119 | 77 | Apparente power fase 2 | VA | Signed integer 16 bits
120 | 78 | Apparente power fase 3 | VA | Signed integer 16 bits
121 | 79 | Apparente power total | VA | Signed integer 16 bits
122 | 7A | Power factor phase 1 |  | Signed integer 16 bits
123 | 7B | Power factor phase 2 |  | Signed integer 16 bits
124 | 7C | Power factor phase 3 |  | Signed integer 16 bits
125 | 7D | Power factor phase total |  | Signed integer 16 bits
126 | 7E | Frequency | Hz | Signed integer 16 bits
127 | 7F | Direct active energy MWh in *1 | MWh | Unsigned integer 16 bits
128 | 80 | Direct active energy kWh in *1 | kWh | Unsigned integer 16 bits
129 | 81 | Direct active energy Wh in *1 | Wh | Unsigned integer 16 bits
130 | 82 | Direct reactive energy Mvarh in *1 | Mvarh | Unsigned integer 16 bits
131 | 83 | Direct reactive energy kvarh in *1 | kvarh | Unsigned integer 16 bits
132 | 84 | Direct reactive energy varh in *1 | varh | Unsigned integer 16 bits
133 | 85 | Reverse active energy MWh in *1 | MWh | Unsigned integer 16 bits
134 | 86 | Reverse active energy kWh in *1 | kWh | Unsigned integer 16 bits
135 | 87 | Reverse active energy Wh in *1 | Wh | Unsigned integer 16 bits
136 | 88 | Reverse reactive energy Mvarh in *1 | Mvarh | Unsigned integer 16 bits
137 | 89 | Reverse reactive energy kvarh in *1 | kvarh | Unsigned integer 16 bits
138 | 8A | Reverse reactive energy varh in *1 | varh | Unsigned integer 16 bits
139 | 8B | Angle Phi1 | Degree | Signed integer 16 bits
140 | 8C | Angle Phi2 | Degree | Signed integer 16 bits
141 | 8D | Angle Phi3 | Degree | Signed integer 16 bits
142 | 8E | Angle Phi total | Degree | Signed integer 16 bits
143 | 8F | Current demand phase 1 | A | Signed integer 16 bits
144 | 90 | Current demand phase 2 | A | Signed integer 16 bits
145 | 91 | Current demand phase 3 | A | Signed integer 16 bits
146 | 92 | Active power demand | W | Signed integer 16 bits
147 | 93 | Reactive power demand | var | Signed integer 16 bits
148 | 94 | Apparent power demand | VA | Signed integer 16 bits
149 | 95 | Voltage angle phase 1 | Degree | Signed integer 16 bits
150 | 96 | Voltage angle phase 2 | Degree | Signed integer 16 bits
151 | 97 | Voltage angle phase 3 | Degree | Signed integer 16 bits
152 | 98 | Currente angle phase 1 | Degree | Signed integer 16 bits
153 | 99 | Currente angle phase 2 | Degree | Signed integer 16 bits
154 | 9A | Currente angle phase 3 | Degree | Signed integer 16 bits
155 | 9B | Displacement factor phase 1 |  | Signed integer 16 bits
156 | 9C | Displacement factor phase 2 |  | Signed integer 16 bits
157 | 9D | Displacement factor phase 3 |  | Signed integer 16 bits
158 | 9E | Displacement factor phase total |  | Signed integer 16 bits
159 | 9F | THD U1 | % | Signed integer 16 bits
160 | A0 | THD U 2 | % | Signed integer 16 bits
161 | A1 | THD U 3 | % | Signed integer 16 bits
162 | A2 | THD I1 | % | Signed integer 16 bits
163 | A3 | THD I2 | % | Signed integer 16 bits
164 | A4 | THD I3 | % | Signed integer 16 bits
165 | A5 | Apparente energy MVAh *1 | MVAh | Signed integer 16 bits
166 | A6 | Apparente energy kVAh *1 | MVAh | Signed integer 16 bits
167 | A7 | Apparente energy VAh *1 | MVAh | Signed integer 16 bits
168 | A8 | Umbalance phase voltage | % | Signed integer 16 bits
169 | A9 | Umbalance line voltage | % | Signed integer 16 bits
170 | AA | Umbalance currente | % | Signed integer 16 bits

## BR Legacy 2
Reg[Dec] | Reg[Hex] | Measurement description | Unit | Format
12288 | 3000 | Voltage L1 and Neutral | V | Float 32 bits
12290 | 3002 | Voltage L2 and Neutral | V | Float 32 bits
12292 | 3004 | Voltage L3 and Neutral | V | Float 32 bits
12294 | 3006 | Voltage L1 and L2 | V | Float 32 bits
12296 | 3008 | Voltage L2 and L3 | V | Float 32 bits
12298 | 300A | Voltage L3 and L1 | V | Float 32 bits
12300 | 300C | Three phase system voltage | V | Float 32 bits
12302 | 300E | Reserved
12304 | 3010 | Current phase 1 | A | Float 32 bits
12306 | 3012 | Current phase 2 | A | Float 32 bits
12308 | 3014 | Current phase 3 | A | Float 32 bits
12310 | 3016 | Neutral current | A | Float 32 bits
12312 | 3018 | Three phase system current | A | Float 32 bits
12314 | 301A | Reserved
12316 | 301C | Active power phase 1 | W | Float 32 bits
12318 | 301E | Active power phase 2 | W | Float 32 bits
12320 | 3020 | Active power phase 3 | W | Float 32 bits
12322 | 3022 | Active power total | W | Float 32 bits
12324 | 3024 | Reactive power phase 1 | Var | Float 32 bits
12326 | 3026 | Reactive power phase 2 | Var | Float 32 bits
12328 | 3028 | Reactive power phase 3 | Var | Float 32 bits
12330 | 302A | Reactive power total | Var | Float 32 bits
12332 | 302C | Apparente power fase 1 | VA | Float 32 bits
12334 | 302E | Apparente power fase 2 | VA | Float 32 bits
12336 | 3030 | Apparente power fase 3 | VA | Float 32 bits
12338 | 3032 | Apparente power total | VA | Float 32 bits
12340 | 3034 | Reserved
12342 | 3036 | Power factor phase 1 |  | Float 32 bits
12344 | 3038 | Power factor phase 2 |  | Float 32 bits
12346 | 303A | Power factor phase 3 |  | Float 32 bits
12348 | 303C | Power factor phase total |  | Float 32 bits
12350 | 303E | Displacement factor phase 1 |  | Float 32 bits
12352 | 3040 | Displacement factor phase 2 |  | Float 32 bits
12354 | 3042 | Displacement factor phase 3 |  | Float 32 bits
12356 | 3044 | Displacement factor phase total |  | Float 32 bits
12358 | 3046 | Angle Phi1 |  | Float 32 bits
12360 | 3048 | Angle Phi2 |  | Float 32 bits
12362 | 304A | Angle Phi3 |  | Float 32 bits
12364 | 304C | Angle Phi total |  | Float 32 bits
12366 | 304E | Frequency | Hz | Float 32 bits
12368 | 3050 | Current demand phase 1 | A | Float 32 bits
12370 | 3052 | Current demand phase 2 | A | Float 32 bits
12372 | 3054 | Current demand phase 3 | A | Float 32 bits
12374 | 3056 | Active power demand | W | Float 32 bits
12376 | 3058 | Reactive power demand | Var | Float 32 bits
12378 | 305A | Apparent power demand | VA | Float 32 bits
12380 | 305C | Voltage angle phase 1 |  | Float 32 bits
12382 | 305E | Voltage angle phase 2 |  | Float 32 bits
12384 | 3060 | Voltage angle phase 3 |  | Float 32 bits
12386 | 3062 | Currente angle phase 1 |  | Float 32 bits
12388 | 3064 | Currente angle phase 2 |  | Float 32 bits
12390 | 3066 | Currente angle phase 3 |  | Float 32 bits
12392 | 3068 | THD U1 | % | Float 32 bits
12394 | 306A | THD U 2 | % | Float 32 bits
12396 | 306C | THD U 3 | % | Float 32 bits
12398 | 306E | THD I1 | % | Float 32 bits
12400 | 3070 | THD I2 | % | Float 32 bits
12402 | 3072 | THD I3 | % | Float 32 bits
12404 | 3074 | Umbalance phase voltage | % | Float 32 bits
12406 | 3076 | Umbalance line voltage | % | Float 32 bits
12408 | 3078 | Umbalance currente | % | Float 32 bits
12410 | 307A | Direct active energy kWh in *100 | kWh | Unsigned integer 32 bits
12412 | 307C | Reverse active energy kWh in *100 | kvarh | Unsigned integer 32 bits
12414 | 307E | Direct reactive energy kWh in *100 | kWh | Unsigned integer 32 bits
12416 | 3080 | Reverse reactive energy kWh in *100 | kvarh | Unsigned integer 32 bits
12418 | 3082 | Apparente energy kVAh *100 | kVAh | Unsigned integer 32 bits
12420 | 3084 | Average Voltage L1 and Neutral | V | Float 32 bits
12422 | 3086 | Average Voltage L2 and Neutral | V | Float 32 bits
12424 | 3088 | Average Voltage L3 and Neutral | V | Float 32 bits
12426 | 308A | Average Voltage L1 and L2 | V | Float 32 bits
12428 | 308C | Average Voltage L2 and L3 | V | Float 32 bits
12430 | 308E | Average Voltage L3 and L1 | V | Float 32 bits
12432 | 3090 | Average Current phase 1 | A | Float 32 bits
12434 | 3092 | Average Current phase 2 | A | Float 32 bits
12436 | 3094 | Average Current phase 3 | A | Float 32 bits
12438 | 3096 | Average Neutral current | A | Float 32 bits
12440 | 3098 | Average Active power phase 1 | W | Float 32 bits
12442 | 309A | Average Active power phase 2 | W | Float 32 bits
12444 | 309C | Average Active power phase 3 | W | Float 32 bits
12446 | 309E | Average Active power total | W | Float 32 bits
12448 | 30A0 | Average Reactive power phase 1 | Var | Float 32 bits
12450 | 30A2 | Average Reactive power phase 2 | Var | Float 32 bits
12452 | 30A4 | Average Reactive power phase 3 | Var | Float 32 bits
12454 | 30A6 | Average Reactive power total | Var | Float 32 bits
12456 | 30A8 | Average Apparente power fase 1 | VA | Float 32 bits
12458 | 30AA | Average Apparente power fase 2 | VA | Float 32 bits
12460 | 30AC | Average Apparente power fase 3 | VA | Float 32 bits
12462 | 30AE | Average Apparente power total | VA | Float 32 bits
12464 | 30B0 | Maximum Voltage L1 and Neutral | V | Float 32 bits
12466 | 30B2 | Maximum Voltage L2 and Neutral | V | Float 32 bits
12468 | 30B4 | Maximum Voltage L3 and Neutral | V | Float 32 bits
12470 | 30B6 | Maximum Voltage L1 and L2 | V | Float 32 bits
12472 | 30B8 | Maximum Voltage L2 and L3 | V | Float 32 bits
12474 | 30BA | Maximum Voltage L3 and L1 | V | Float 32 bits
12476 | 30BC | Maximum Current phase 1 | A | Float 32 bits
12478 | 30BE | Maximum Current phase 2 | A | Float 32 bits
12480 | 30C0 | Maximum Current phase 3 | A | Float 32 bits
12482 | 30C2 | Maximum Neutral current | A | Float 32 bits
12484 | 30C4 | Maximum Active power phase 1 | W | Float 32 bits
12486 | 30C6 | Maximum Active power phase 2 | W | Float 32 bits
12488 | 30C8 | Maximum Active power phase 3 | W | Float 32 bits
12490 | 30CA | Maximum Active power total | W | Float 32 bits
12492 | 30CC | Maximum Reactive power phase 1 | Var | Float 32 bits
12494 | 30CE | Maximum Reactive power phase 2 | Var | Float 32 bits
12496 | 30D0 | Maximum Reactive power phase 3 | Var | Float 32 bits
12498 | 30D2 | Maximum Reactive power total | Var | Float 32 bits
12500 | 30D4 | Maximum Apparente power fase 1 | VA | Float 32 bits
12502 | 30D6 | Maximum Apparente power fase 2 | VA | Float 32 bits
12504 | 30D8 | Maximum Apparente power fase 3 | VA | Float 32 bits
12506 | 30DA | Maximum Apparente power total | VA | Float 32 bits
12508 | 30DC | Minimum Voltage L1 and Neutral | V | Float 32 bits
12510 | 30DE | Minimum Voltage L2 and Neutral | V | Float 32 bits
12512 | 30E0 | Minimum Voltage L3 and Neutral | V | Float 32 bits
12514 | 30E2 | Minimum Voltage L1 and L2 | V | Float 32 bits
12516 | 30E4 | Minimum Voltage L2 and L3 | V | Float 32 bits
12518 | 30E6 | Minimum Voltage L3 and L1 | V | Float 32 bits
12520 | 30E8 | Minimum Current phase 1 | A | Float 32 bits
12522 | 30EA | Minimum Current phase 2 | A | Float 32 bits
12524 | 30EC | Minimum Current phase 3 | A | Float 32 bits
12526 | 30EE | Minimum Neutral current | A | Float 32 bits
12528 | 30F0 | Minimum Active power phase 1 | W | Float 32 bits
12530 | 30F2 | Minimum Active power phase 2 | W | Float 32 bits
12532 | 30F4 | Minimum Active power phase 3 | W | Float 32 bits
12534 | 30F6 | Minimum Active power total | W | Float 32 bits
12536 | 30F8 | Minimum Reactive power phase 1 | Var | Float 32 bits
12538 | 30FA | Minimum Reactive power phase 2 | Var | Float 32 bits
12540 | 30FC | Minimum Reactive power phase 3 | Var | Float 32 bits
12542 | 30FE | Minimum Reactive power total | Var | Float 32 bits
12544 | 3100 | Minimum Apparente power fase 1 | VA | Float 32 bits
12546 | 3102 | Minimum Apparente power fase 2 | VA | Float 32 bits
12548 | 3104 | Minimum Apparente power fase 3 | VA | Float 32 bits
12550 | 3106 | Minimum Apparente power total | VA | Float 32 bits
Reg[dec] | Reg[hex] | Block configuration for historical |  | Data type
16576 | 40C0 | Indicator | 1 | integer 16
16577 | 40C1 | Number os variables in the block |  | integer 16
16578 | 40C2 | Sample time [minutes] |  | integer 16
16579 | 40C3 | Variables linked ID to the historical data 1 |  | integer 16
16580 | 40C4 | Variables linked ID to the historical data 1 |  | integer 16
16608 | 40E0 | Variables linked ID to the historical data 40 |  | integer 16
16619 | 40EB | Variables linked ID to the historical data 41 |  | integer 16
Reg[dec] | Reg[hex] | Header for historical |  | Data type
16624 | 40F0 | Function |  | 0x0001 - Read actual value 0x0002 - Read data at address 0x0003 - Read data at start adress and increment the possition 0x0004 - Read data at start adress and decrement the possition
16625 | 40F1 | Function complement |  | 0xXXXX - Position
Reg[dec] | Reg[hex] | Data block for historical |  | Data type
16640 | 4100 | Variable linked to historial |  | Float 32 bits
16642 | 4102 | Variable linked to historial |  | Float 32 bits
16644 | 4104 | Variable linked to historial |  | Float 32 bits
16646 | 4106 | Variable linked to historial |  | Float 32 bits
16648 | 4108 | Variable linked to historial |  | Float 32 bits
16650 | 410A | Variable linked to historial |  | Float 32 bits
16652 | 410C | Variable linked to historial |  | Float 32 bits
16654 | 410E | Variable linked to historial |  | Float 32 bits
16656 | 4110 | Variable linked to historial |  | Float 32 bits
16658 | 4112 | Variable linked to historial |  | Float 32 bits
16660 | 4114 | Variable linked to historial |  | Float 32 bits
16662 | 4116 | Variable linked to historial |  | Float 32 bits
16664 | 4118 | Variable linked to historial |  | Float 32 bits
16666 | 411A | Variable linked to historial |  | Float 32 bits
16668 | 411C | Variable linked to historial |  | Float 32 bits
16670 | 411E | Variable linked to historial |  | Float 32 bits
16672 | 4120 | Variable linked to historial |  | Float 32 bits
16674 | 4122 | Variable linked to historial |  | Float 32 bits
16676 | 4124 | Variable linked to historial |  | Float 32 bits
16678 | 4126 | Variable linked to historial |  | Float 32 bits
16680 | 4128 | Variable linked to historial |  | Float 32 bits
16682 | 412A | Variable linked to historial |  | Float 32 bits
16684 | 412C | Variable linked to historial |  | Float 32 bits
16686 | 412E | Variable linked to historial |  | Float 32 bits
16688 | 4130 | Variable linked to historial |  | Float 32 bits
16690 | 4132 | Variable linked to historial |  | Float 32 bits
16692 | 4134 | Variable linked to historial |  | Float 32 bits
16694 | 4136 | Variable linked to historial |  | Float 32 bits
16696 | 4138 | Variable linked to historial |  | Float 32 bits
16698 | 413A | Variable linked to historial |  | Float 32 bits
16700 | 413C | Variable linked to historial |  | Float 32 bits
16702 | 413E | Variable linked to historial |  | Float 32 bits
16704 | 4140 | Variable linked to historial |  | Float 32 bits
16706 | 4142 | Variable linked to historial |  | Float 32 bits
16708 | 4144 | Variable linked to historial |  | Float 32 bits
16710 | 4146 | Variable linked to historial |  | Float 32 bits
16712 | 4148 | Variable linked to historial |  | Float 32 bits
16714 | 414A | Variable linked to historial |  | Float 32 bits
16716 | 414C | Variable linked to historial |  | Float 32 bits
16718 | 414E | Variable linked to historial |  | Float 32 bits
16720 | 4150 | Variable linked to historial |  | Float 32 bits
RTC
16720 | 4150 | Seconds 0 to 59 |  | Integer 16
16721 | 4151 | Minutes 0 to 59 |  | Integer 16
16723 | 4153 | Hours 0 to 24 |  | Integer 16
16725 | 4155 | Days 1 to 31 |  | Integer 16
16727 | 4157 | Weekdays 0 to 60 |  | Integer 16
16729 | 4159 | Months 1 to 12 |  | Integer 16
16731 | 415B | Years 0 to 99 |  | Integer 16
Reg [Dec] | Reg [Hex] | Configuration for read mode of demand analysis data
16735 | 415F | Function |  | 0x0001 - Read actual value 0x0002 - Read data at address 0x0003 - Read data at start adress and increment the possition 0x0004 - Read data at start adress and decrement the possition
16736 | 4160 | Function complement |  | 0xXXXX - Position
Data block for historical
16737 | 4161 | Time stap Max Active Demand
16738 | 4162 | Time stap Max Active Demand
16739 | 4163 | Valuer Max Active Demand
16740 | 4164 | Valuer Max Active Demand
16741 | 4165 | Time stap Max Reactive Demand
16742 | 4166 | Time stap Max Reactive Demand
16743 | 4167 | Valuer Max Reactive Demand
16744 | 4168 | Valuer Max Reactive Demand
16745 | 4169 | Time stap Max Apparent Demand
16746 | 416A | Time stap Max Apparent Demand
16747 | 416B | Valuer Max Apparent Demand
16748 | 416C | Valuer Max Apparent Demand
16749 | 416D | CRC 16

## M2M Legacy
Reg[Dec] | Reg[Hex] | Measurement description | Unit | Format
4096 | 1000 | 3-PHASE SYSTEM VOLTAGE | V | Unsigned integer 32 bits
4098 | 1002 | PHASE VOLTAGE L1-N | V | Unsigned integer 32 bits
4100 | 1004 | PHASE VOLTAGE L2-N | V | Unsigned integer 32 bits
4102 | 1006 | PHASE VOLTAGE L3-N | V | Unsigned integer 32 bits
4104 | 1008 | LINE VOLTAGE L1-2 | V | Unsigned integer 32 bits
4106 | 100A | LINE VOLTAGE L2-3 | V | Unsigned integer 32 bits
4108 | 100C | LINE VOLTAGE L3-1 | V | Unsigned integer 32 bits
4110 | 100E | 3-PHASE SYSTEM CURRENT | mA | Unsigned integer 32 bits
4112 | 1010 | LINE CURRENT L1 | mA | Unsigned integer 32 bits
4114 | 1012 | LINE CURRENT L2 | mA | Unsigned integer 32 bits
4116 | 1014 | LINE CURRENT L3 | mA | Unsigned integer 32 bits
4118 | 1016 | 3-PHASE SYS. POWER FACTOR | * 1000 | Signed integer 32 bits
4120 | 1018 | POWER FACTOR L1 | * 1000 | Signed integer 32 bits
4122 | 101A | POWER FACTOR L2 | * 1000 | Signed integer 32 bits
4124 | 101C | POWER FACTOR L3 | * 1000 | Signed integer 32 bits
4126 | 101E | 3-PHASE SYSTEM COS Phi | * 1000 | Signed integer 32 bits
4128 | 1020 | PHASE COS Phi1 | * 1000 | Signed integer 32 bits
4130 | 1022 | PHASE COS Phi2 | * 1000 | Signed integer 32 bits
4132 | 1024 | PHASE COS Phi3 | * 1000 | Signed integer 32 bits
4134 | 1026 | 3-PHASE S. APPARENT POWER | VA | Unsigned integer 32 bits
4136 | 1028 | APPARENT POWER L1 | VA | Unsigned integer 32 bits
4138 | 102A | APPARENT POWER L2 | VA | Unsigned integer 32 bits
4140 | 102C | APPARENT POWER L3 | VA | Unsigned integer 32 bits
4142 | 102E | 3-PHASE SYS. ACTIVE POWER | W | Signed integer 32 bits
4144 | 1030 | ACTIVE POWER L1 | W | Signed integer 32 bits
4146 | 1032 | ACTIVE POWER L2 | W | Signed integer 32 bits
4148 | 1034 | ACTIVE POWER L3 | W | Signed integer 32 bits
4150 | 1036 | 3-PHASE S. REACTIVE POWER | VAr | Signed integer 32 bits
4152 | 1038 | REACTIVE POWER L1 | VAr | Signed integer 32 bits
4154 | 103A | REACTIVE POWER L2 | VAr | Signed integer 32 bits
4156 | 103C | REACTIVE POWER L3 | VAr | Signed integer 32 bits
4158 | 103E | 3-PHASE SYS. ACTIVE ENERGY | Wh*100 | Unsigned integer 32 bits
4160 | 1040 | 3-PHASE S. REACTIVE ENERGY | Varh*100 | Unsigned integer 32 bits
4162 | 1042 | Neutral current | mA | Unsigned integer 32 bits
4166 | 1046 | FREQUENCY | mHz | Unsigned integer 32 bits
4168 | 1048 | 3-Phase sys. angle between current and voltage | m Degress | Signed integer 32 bits
4170 | 104A | Phase 1 angle between current and voltage | m Degress | Signed integer 32 bits
4172 | 104C | Phase 2 angle between current and voltage | m Degress | Signed integer 32 bits
4174 | 104E | Phase 3 angle between current and voltage | m Degress | Signed integer 32 bits
4176 | 1050 | Voltage angle phase 1 | m Degress | Signed integer 32 bits
4178 | 1052 | Voltage angle phase 2 | m Degress | Signed integer 32 bits
4180 | 1054 | Voltage angle phase 3 | m Degress | Signed integer 32 bits
4182 | 1056 | Currente angle phase 1 | m Degress | Signed integer 32 bits
4184 | 1058 | Currente angle phase 2 | m Degress | Signed integer 32 bits
4186 | 105A | Currente angle phase 3 | m Degress | Signed integer 32 bits
4202 | 106A | Umbalance phase voltage | % * 100 | Unsigned integer 32 bits
4204 | 106C | Umbalance line voltage | % * 100 | Unsigned integer 32 bits
4206 | 106E | Umbalance current | % * 100 | Unsigned integer 32 bits
4208 | 1070 | 3-PHASE SYS. ACTIVE POWER 15’ AVER | Watt | Signed Long ( S )
4210 | 1072 | 3-PHASE SYS. APPARENT POWER 15’ AVER | VA | Unsigned integer 32 bits
4226 | 1082 | VOLTAGE ThdF L1 (NORMAL VISUALISATION) | * 100 | Unsigned integer 32 bits
4228 | 1084 | VOLTAGE ThdF L2 (NORMAL VISUALISATION) | * 100 | Unsigned integer 32 bits
4230 | 1086 | VOLTAGE ThdF L3 (NORMAL VISUALISATION) | * 100 | Unsigned integer 32 bits
4232 | 1088 | CURRENT ThdF L1 (NORMAL VISUALISATION) | * 100 | Unsigned integer 32 bits
4234 | 108A | CURRENT ThdF L2 (NORMAL VISUALISATION) | * 100 | Unsigned integer 32 bits
4236 | 108C | CURRENT ThdF L3 (NORMAL VISUALISATION) | * 100 | Unsigned integer 32 bits
4262 | 10A6 | 3-PHASE SYS. APPARENT ENERGY | Vah*100 | Unsigned integer 32 bits
4270 | 10AE | 3-PHASE SYS. GENERATED ACTIVE ENERGY | Wh*100 | Unsigned integer 32 bits
4278 | 10B6 | 3-PHASE S. GENERATED REACTIVE ENERGY | Varh*100 | Unsigned integer 32 bits
4294 | 10C6 | Current 15' Averange L1 | mA | Unsigned integer 32 bits
4296 | 10C8 | Current 15' Averange L2 | mA | Unsigned integer 32 bits
4298 | 10CA | Current 15' Averange L3 | mA | Unsigned integer 32 bits
4512 | 11A0 | CURRENT TRANSFORM RATIO (CT) | 1-2000 | Unsigned integer 32 bits
4514 | 11A2 | VOLTAGE TRANSFORM RATIO (VT) | 1-600 | Unsigned integer 32 bits
4516 | 11A4 | PULSE ENERGY WEIGHT | 1-4 | Unsigned integer 32 bits