## Mapping Table
Parameter | Unit | Details | Resolution | Data Type | Access | Register (Hex) | Reg (Dec) | Nr of quantities | Size | Nr of registers | Product Type | Functionality group
Active energy - import | kWh |  | 0.01 | Unsigned | Read | 5000 | 20480 | 1 | 4 | 4 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Energy (total)
Active energy - export | kWh |  | 0.01 | Unsigned | Read | 5004 | 20484 | 1 | 4 | 4 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Energy (total)
Active energy - net | kWh |  | 0.01 | Signed | Read | 5008 | 20488 | 1 | 4 | 4 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Energy (total)
Reactive energy - import | kvarh |  | 0.01 | Unsigned | Read | 500C | 20492 | 1 | 4 | 4 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Energy (total)
Reactive energy - export | kvarh |  | 0.01 | Unsigned | Read | 5010 | 20496 | 1 | 4 | 4 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Energy (total)
Reactive energy - net | kvarh |  | 0.01 | Signed | Read | 5014 | 20500 | 1 | 4 | 4 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Energy (total)
Apparent energy - import | kVA |  | 0.01 | Unsigned | Read | 5018 | 20504 | 1 | 4 | 4 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Energy (total)
Apparent energy - export | kVA |  | 0.01 | Unsigned | Read | 501C | 20508 | 1 | 4 | 4 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Energy (total)
Apparent energy - net | kVA |  | 0.01 | Signed | Read | 5020 | 20512 | 1 | 4 | 4 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Energy (total)
Active energy - import | kg / kWh | CO2 conversion factor | 0.001 | Unsigned | Read | 5024 | 20516 | 1 | 4 | 4 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Energy Conversion
Active energy - import | Currency / kWh | Currency conversion factor | 0.001 | Unsigned | Read | 5034 | 20532 | 1 | 4 | 4 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Energy Conversion
Active energy - import (Tariffs) | kWh | Tariff from 1 to 6 | 0.01 | Unsigned | Read | 5170 | 20848 | 6 | 4 | 24 | M4M 30 (all versions) | Data Reading - Energy (per tariff)
Active energy - export (Tariffs) | kWh | Tariff from 1 to 6 | 0.01 | Unsigned | Read | 5190 | 20880 | 6 | 4 | 24 | M4M 30 (all versions) | Data Reading - Energy (per tariff)
Reactive energy - import (Tariffs) | kvarh | Tariff from 1 to 6 | 0.01 | Unsigned | Read | 51B0 | 20912 | 6 | 4 | 24 | M4M 30 (all versions) | Data Reading - Energy (per tariff)
Reactive energy - export (Tariffs) | kvarh | Tariff from 1 to 6 | 0.01 | Unsigned | Read | 51D0 | 20944 | 6 | 4 | 24 | M4M 30 (all versions) | Data Reading - Energy (per tariff)
Active energy - import | kWh | L1, L2, L3 | 0.01 | Unsigned | Read | 5460 | 21600 | 3 | 4 | 12 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Energy (per phase)
Active energy - export | kWh | L1, L2, L3 | 0.01 | Unsigned | Read | 546C | 21612 | 3 | 4 | 12 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Energy (per phase)
Active energy - net | kWh | L1, L2, L3 | 0.01 | Signed | Read | 5478 | 21624 | 3 | 4 | 12 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Energy (per phase)
Reactive energy - import | kvarh | L1, L2, L3 | 0.01 | Unsigned | Read | 5484 | 21636 | 3 | 4 | 12 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Energy (per phase)
Reactive energy - export | kvarh | L1, L2, L3 | 0.01 | Unsigned | Read | 5490 | 21648 | 3 | 4 | 12 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Energy (per phase)
Reactive energy - net | kvarh | L1, L2, L3 | 0.01 | Signed | Read | 549C | 21660 | 3 | 4 | 12 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Energy (per phase)
Apparent energy - import | kVA | L1, L2, L3 | 0.01 | Unsigned | Read | 54A8 | 21672 | 3 | 4 | 12 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Energy (per phase)
Apparent energy - export | kVA | L1, L2, L3 | 0.01 | Unsigned | Read | 54B4 | 21684 | 3 | 4 | 12 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Energy (per phase)
Apparent energy - net | kVA | L1, L2, L3 | 0.01 | Signed | Read | 54C0 | 21696 | 3 | 4 | 12 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Energy (per phase)
Three phase system voltage | V |  | 0.1 | Unsigned | Read | 5B00 | 23296 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Phase voltage L1 | V | L1 | 0.1 | Unsigned | Read | 5B02 | 23298 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Phase voltage L2 | V | L2 | 0.1 | Unsigned | Read | 5B04 | 23300 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Phase voltage L3 | V | L3 | 0.1 | Unsigned | Read | 5B06 | 23302 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Line voltage L1-L2 | V | L1-L2 | 0.1 | Unsigned | Read | 5B08 | 23304 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Line voltage L3-L2 | V | L3-L2 | 0.1 | Unsigned | Read | 5B0A | 23306 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Line voltage L1-L3 | V | L1-L3 | 0.1 | Unsigned | Read | 5B0C | 23308 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Three phase system current | A |  | 0.01 | Unsigned | Read | 5B0E | 23310 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Current | A | L1 | 0.01 | Unsigned | Read | 5B10 | 23312 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Current | A | L2 | 0.01 | Unsigned | Read | 5B12 | 23314 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Current | A | L3 | 0.01 | Unsigned | Read | 5B14 | 23316 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Current | A | N | 0.01 | Unsigned | Read | 5B16 | 23318 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Active power | W | Total | 0.01 | Signed | Read | 5B1A | 23322 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Active power | W | L1 | 0.01 | Signed | Read | 5B1C | 23324 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Active power | W | L2 | 0.01 | Signed | Read | 5B1E | 23326 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Active power | W | L3 | 0.01 | Signed | Read | 5B20 | 23328 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Reactive power | var | Total | 0.01 | Signed | Read | 5B22 | 23330 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Reactive power | var | L1 | 0.01 | Signed | Read | 5B24 | 23332 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Reactive power | var | L2 | 0.01 | Signed | Read | 5B26 | 23334 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Reactive power | var | L3 | 0.01 | Signed | Read | 5B28 | 23336 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Apparent power | VA | Total | 0.01 | Signed | Read | 5B2A | 23338 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Apparent power | VA | L1 | 0.01 | Signed | Read | 5B2C | 23340 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Apparent power | VA | L2 | 0.01 | Signed | Read | 5B2E | 23342 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Apparent power | VA | L3 | 0.01 | Signed | Read | 5B30 | 23344 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Frequency | Hz |  | 0.01 | Unsigned | Read | 5B32 | 23346 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Phase angles power | ° | Total, L1, L2, L3 | 0.1 | Signed | Read | 5B33 | 23347 | 4 | 1 | 4 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Phase angles voltage | ° | L1, L2, L3 | 0.1 | Signed | Read | 5B37 | 23351 | 3 | 1 | 3 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Phase angles current | ° | L1, L2, L3 | 0.1 | Signed | Read | 5B3D | 23357 | 3 | 1 | 3 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Power factors |  | Total | 0.001 | Signed | Read | 5B40 | 23360 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Power factors |  | L1 | 0.001 | Signed | Read | 5B41 | 23361 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Power factors |  | L2 | 0.001 | Signed | Read | 5B42 | 23362 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Power factors |  | L3 | 0.001 | Signed | Read | 5B43 | 23363 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Current quadrant |  | Total, L1, L2, L3 | 1 | Unsigned | Read | 5B44 | 23364 | 4 | 1 | 4 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Cosphi (displacement factor) | ° | Total | 0.001 | Signed | Read | 5B48 | 23368 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Cosphi (displacement factor) | ° | L1 | 0.001 | Signed | Read | 5B49 | 23369 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Cosphi (displacement factor) | ° | L2 | 0.001 | Signed | Read | 5B4A | 23370 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Cosphi (displacement factor) | ° | L3 | 0.001 | Signed | Read | 5B4B | 23371 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Average current L1 | A | Data value | 0.01 | Unsigned | Read | 5BD4 | 23508 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Average current L2 | A | Data value | 0.01 | Unsigned | Read | 5BD6 | 23510 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Average current L3 | A | Data value | 0.01 | Unsigned | Read | 5BD8 | 23512 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Average current neutral | A | Data value | 0.01 | Unsigned | Read | 5BDA | 23514 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Average voltage L1 | V | Data value | 0.1 | Unsigned | Read | 5BDC | 23516 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Average voltage L2 | V | Data value | 0.1 | Unsigned | Read | 5BDE | 23518 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Average voltage L3 | V | Data value | 0.1 | Unsigned | Read | 5BE0 | 23520 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Average voltage L1-L2 | V | Data value | 0.1 | Unsigned | Read | 5BE2 | 23522 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Average voltage L2-L3 | V | Data value | 0.1 | Unsigned | Read | 5BE4 | 23524 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Average voltage L1-L3 | V | Data value | 0.1 | Unsigned | Read | 5BE6 | 23526 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Average active power total | W | Data value | 0.01 | Signed | Read | 5BE8 | 23528 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Average active power L1 | W | Data value | 0.01 | Signed | Read | 5BEA | 23530 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Average active power L2 | W | Data value | 0.01 | Signed | Read | 5BEC | 23532 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Average active power L3 | W | Data value | 0.01 | Signed | Read | 5BEE | 23534 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Average reactive power total | var | Data value | 0.01 | Signed | Read | 5BF0 | 23536 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Average reactive power L1 | var | Data value | 0.01 | Signed | Read | 5BF2 | 23538 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Average reactive power L2 | var | Data value | 0.01 | Signed | Read | 5BF4 | 23540 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Average reactive power L3 | var | Data value | 0.01 | Signed | Read | 5BF6 | 23542 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Average apparent power total | VA | Data value | 0.01 | Signed | Read | 5BF8 | 23544 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Average apparent power L1 | VA | Data value | 0.01 | Signed | Read | 5BFA | 23546 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Average apparent power L2 | VA | Data value | 0.01 | Signed | Read | 5BFC | 23548 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Average apparent power L3 | VA | Data value | 0.01 | Signed | Read | 5BFE | 23550 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum current L1 | A | Data value | 0.01 | Unsigned | Read | 5C10 | 23568 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum current L2 | A | Data value | 0.01 | Unsigned | Read | 5C12 | 23570 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum current L3 | A | Data value | 0.01 | Unsigned | Read | 5C14 | 23572 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum current neutral | A | Data value | 0.01 | Unsigned | Read | 5C16 | 23574 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum voltage L1 | V | Data value | 0.1 | Unsigned | Read | 5C18 | 23576 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum voltage L2 | V | Data value | 0.1 | Unsigned | Read | 5C1A | 23578 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum voltage L3 | V | Data value | 0.1 | Unsigned | Read | 5C1C | 23580 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum voltage L1-L2 | V | Data value | 0.1 | Unsigned | Read | 5C1E | 23582 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum voltage L2-L3 | V | Data value | 0.1 | Unsigned | Read | 5C20 | 23584 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum voltage L1-L3 | V | Data value | 0.1 | Unsigned | Read | 5C22 | 23586 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum active power total | W | Data value | 0.01 | Signed | Read | 5C24 | 23588 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum active power L1 | W | Data value | 0.01 | Signed | Read | 5C26 | 23590 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum active power L2 | W | Data value | 0.01 | Signed | Read | 5C28 | 23592 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum active power L3 | W | Data value | 0.01 | Signed | Read | 5C2A | 23594 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum reactive power total | var | Data value | 0.01 | Signed | Read | 5C2C | 23596 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum reactive power L1 | var | Data value | 0.01 | Signed | Read | 5C2E | 23598 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum reactive power L2 | var | Data value | 0.01 | Signed | Read | 5C30 | 23600 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum reactive power L3 | var | Data value | 0.01 | Signed | Read | 5C32 | 23602 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum apparent power total | VA | Data value | 0.01 | Signed | Read | 5C34 | 23604 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum apparent power L1 | VA | Data value | 0.01 | Signed | Read | 5C36 | 23606 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum apparent power L2 | VA | Data value | 0.01 | Signed | Read | 5C38 | 23608 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum apparent power L3 | VA | Data value | 0.01 | Signed | Read | 5C3A | 23610 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum current L1 timestamp |  | Timestamp |  | Unsigned | Read | 5C4C | 23628 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum current L2 timestamp |  | Timestamp |  | Unsigned | Read | 5C4E | 23630 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum current L3 timestamp |  | Timestamp |  | Unsigned | Read | 5C50 | 23632 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum current neutral timestamp |  | Timestamp |  | Unsigned | Read | 5C52 | 23634 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum voltage L1 timestamp |  | Timestamp |  | Unsigned | Read | 5C54 | 23636 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum voltage L2 timestamp |  | Timestamp |  | Unsigned | Read | 5C56 | 23638 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum voltage L3 timestamp |  | Timestamp |  | Unsigned | Read | 5C58 | 23640 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum voltage L1-L2 timestamp |  | Timestamp |  | Unsigned | Read | 5C5A | 23642 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum voltage L2-L3 timestamp |  | Timestamp |  | Unsigned | Read | 5C5C | 23644 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum voltage L1-L3 timestamp |  | Timestamp |  | Unsigned | Read | 5C5E | 23646 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum active power total timestamp |  | Timestamp |  | Unsigned | Read | 5C60 | 23648 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum active power L1 timestamp |  | Timestamp |  | Unsigned | Read | 5C62 | 23650 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum active power L2 timestamp |  | Timestamp |  | Unsigned | Read | 5C64 | 23652 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum active power L3 timestamp |  | Timestamp |  | Unsigned | Read | 5C66 | 23654 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum reactive power total timestamp |  | Timestamp |  | Unsigned | Read | 5C68 | 23656 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum reactive power L1 timestamp |  | Timestamp |  | Unsigned | Read | 5C6A | 23658 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum reactive power L2 timestamp |  | Timestamp |  | Unsigned | Read | 5C6C | 23660 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum reactive power L3 timestamp |  | Timestamp |  | Unsigned | Read | 5C6E | 23662 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum apparent power total timestamp |  | Timestamp |  | Unsigned | Read | 5C70 | 23664 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum apparent power L1 timestamp |  | Timestamp |  | Unsigned | Read | 5C72 | 23666 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum apparent power L2 timestamp |  | Timestamp |  | Unsigned | Read | 5C74 | 23668 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Maximum apparent power L3 timestamp |  | Timestamp |  | Unsigned | Read | 5C76 | 23670 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum current L1 | A | Data value | 0.01 | Unsigned | Read | 5C88 | 23688 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum current L2 | A | Data value | 0.01 | Unsigned | Read | 5C8A | 23690 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum current L3 | A | Data value | 0.01 | Unsigned | Read | 5C8C | 23692 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum current neutral | A | Data value | 0.01 | Unsigned | Read | 5C8E | 23694 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum voltage L1 | V | Data value | 0.1 | Unsigned | Read | 5C90 | 23696 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum voltage L2 | V | Data value | 0.1 | Unsigned | Read | 5C92 | 23698 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum voltage L3 | V | Data value | 0.1 | Unsigned | Read | 5C94 | 23700 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum voltage L1-L2 | V | Data value | 0.1 | Unsigned | Read | 5C96 | 23702 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum voltage L2-L3 | V | Data value | 0.1 | Unsigned | Read | 5C98 | 23704 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum voltage L1-L3 | V | Data value | 0.1 | Unsigned | Read | 5C9A | 23706 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum active power total | W | Data value | 0.01 | Signed | Read | 5C9C | 23708 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum active power L1 | W | Data value | 0.01 | Signed | Read | 5C9E | 23710 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum active power L2 | W | Data value | 0.01 | Signed | Read | 5CA0 | 23712 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum active power L3 | W | Data value | 0.01 | Signed | Read | 5CA2 | 23714 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum reactive power total | var | Data value | 0.01 | Signed | Read | 5CA4 | 23716 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum reactive power L1 | var | Data value | 0.01 | Signed | Read | 5CA6 | 23718 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum reactive power L2 | var | Data value | 0.01 | Signed | Read | 5CA8 | 23720 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum reactive power L3 | var | Data value | 0.01 | Signed | Read | 5CAA | 23722 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum apparent power total | VA | Data value | 0.01 | Signed | Read | 5CAC | 23724 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum apparent power L1 | VA | Data value | 0.01 | Signed | Read | 5CAE | 23726 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum apparent power L2 | VA | Data value | 0.01 | Signed | Read | 5CB0 | 23728 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum apparent power L3 | VA | Data value | 0.01 | Signed | Read | 5CB2 | 23730 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum current L1 timestamp |  | Timestamp |  | Unsigned | Read | 5CC4 | 23748 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum current L2 timestamp |  | Timestamp |  | Unsigned | Read | 5CC6 | 23750 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum current L3 timestamp |  | Timestamp |  | Unsigned | Read | 5CC8 | 23752 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum current neutral timestamp |  | Timestamp |  | Unsigned | Read | 5CCA | 23754 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum voltage L1 timestamp |  | Timestamp |  | Unsigned | Read | 5CCC | 23756 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum voltage L2 timestamp |  | Timestamp |  | Unsigned | Read | 5CCE | 23758 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum voltage L3 timestamp |  | Timestamp |  | Unsigned | Read | 5CD0 | 23760 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum voltage L1-L2 timestamp |  | Timestamp |  | Unsigned | Read | 5CD2 | 23762 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum voltage L2-L3 timestamp |  | Timestamp |  | Unsigned | Read | 5CD4 | 23764 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum voltage L1-L3 timestamp |  | Timestamp |  | Unsigned | Read | 5CD6 | 23766 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum active power total timestamp |  | Timestamp |  | Unsigned | Read | 5CD8 | 23768 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum active power L1 timestamp |  | Timestamp |  | Unsigned | Read | 5CDA | 23770 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum active power L2 timestamp |  | Timestamp |  | Unsigned | Read | 5CDC | 23772 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum active power L3 timestamp |  | Timestamp |  | Unsigned | Read | 5CDE | 23774 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum reactive power total timestamp |  | Timestamp |  | Unsigned | Read | 5CE0 | 23776 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum reactive power L1 timestamp |  | Timestamp |  | Unsigned | Read | 5CE2 | 23778 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum reactive power L2 timestamp |  | Timestamp |  | Unsigned | Read | 5CE4 | 23780 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum reactive power L3 timestamp |  | Timestamp |  | Unsigned | Read | 5CE6 | 23782 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum apparent power total timestamp |  | Timestamp |  | Unsigned | Read | 5CE8 | 23784 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum apparent power L1 timestamp |  | Timestamp |  | Unsigned | Read | 5CEA | 23786 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum apparent power L2 timestamp |  | Timestamp |  | Unsigned | Read | 5CEC | 23788 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Minimum apparent power L3 timestamp |  | Timestamp |  | Unsigned | Read | 5CEE | 23790 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Voltage THD harmonics | % | L1 (THD) | 0.1 | Unsigned | Read | 5D00 | 23808 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Power Quality
|  | L1 (2nd,3rd…40th) | 0.1 | Unsigned | Read | 5D01 | 23809 | 39 | 1 | 39 | M4M 30 (all versions) | Data Reading - Power Quality
| % | L2 (THD) | 0.1 | Unsigned | Read | 5D80 | 23936 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Power Quality
|  | L2 (2nd,3rd…40th) | 0.1 | Unsigned | Read | 5D81 | 23937 | 39 | 1 | 39 | M4M 30 (all versions) | Data Reading - Power Quality
| % | L3 (THD) | 0.1 | Unsigned | Read | 5E00 | 24064 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Power Quality
|  | L3 (2nd,3rd…40th) | 0.1 | Unsigned | Read | 5E01 | 24065 | 39 | 1 | 39 | M4M 30 (all versions) | Data Reading - Power Quality
| % | L1-L2 (THD) | 0.1 | Unsigned | Read | 5E80 | 24192 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Power Quality
|  | L1-L2 (2nd,3rd…40th) | 0.1 | Unsigned | Read | 5E81 | 24193 | 39 | 1 | 39 | M4M 30 (all versions) | Data Reading - Power Quality
| % | L3-L2 (THD) | 0.1 | Unsigned | Read | 5F00 | 24320 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Power Quality
|  | L3-L2 (2nd,3rd…40th) | 0.1 | Unsigned | Read | 5F01 | 24321 | 39 | 1 | 39 | M4M 30 (all versions) | Data Reading - Power Quality
| % | L1-L3 (THD) | 0.1 | Unsigned | Read | 5F80 | 24448 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Power Quality
|  | L1-L3 (2nd,3rd…40th) | 0.1 | Unsigned | Read | 5F81 | 24449 | 39 | 1 | 39 | M4M 30 (all versions) | Data Reading - Power Quality
Current harmonics | % | L1 (THD) | 0.1 | Unsigned | Read | 6000 | 24576 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Power Quality
|  | L1 (2nd,3rd…40th) | 0.1 | Unsigned | Read | 6001 | 24577 | 39 | 1 | 39 | M4M 30 (all versions) | Data Reading - Power Quality
| % | L2 (THD) | 0.1 | Unsigned | Read | 6080 | 24704 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Power Quality
|  | L2 (2nd,3rd…40th) | 0.1 | Unsigned | Read | 6081 | 24705 | 39 | 1 | 39 | M4M 30 (all versions) | Data Reading - Power Quality
| % | L3 (THD) | 0.1 | Unsigned | Read | 6100 | 24832 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Power Quality
|  | L3 (2nd,3rd…40th) | 0.1 | Unsigned | Read | 6101 | 24833 | 39 | 1 | 39 | M4M 30 (all versions) | Data Reading - Power Quality
| % | N (THD) | 0.1 | Unsigned | Read | 6180 | 24960 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Power Quality
|  | N (2nd,3rd…40th) | 0.1 | Unsigned | Read | 6181 | 24961 | 39 | 1 | 39 | M4M 30 (all versions) | Data Reading - Power Quality
Unbalances | % | Phase voltage | 0.1 | Unsigned | Read | 6200 | 25088 | 1 | 2 | 2 | M4M 30 (all versions) | Data Reading - Power Quality
| % | Line voltage | 0.1 | Unsigned | Read | 6202 | 25090 | 1 | 2 | 2 | M4M 30 (all versions) | Data Reading - Power Quality
| % | Current | 0.1 | Unsigned | Read | 6204 | 25092 | 1 | 2 | 2 | M4M 30 (all versions) | Data Reading - Power Quality
Outputs | 0: OFF, 1: ON | Output 1 |  |  | Read/Write | 6300 | 25344 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - I/O
| 0: OFF, 1: ON | Output 2 |  |  | Read/Write | 6301 | 25345 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - I/O
| 0: OFF, 1: ON | Output 3 |  |  | Read/Write | 6302 | 25346 | 1 | 1 | 1 | M4M 30 (all versions) | Data Reading - I/O
| 0: OFF, 1: ON | Output 4 |  |  | Read/Write | 6303 | 25347 | 1 | 1 | 1 | M4M 30 (all versions) | Data Reading - I/O
| 0: OFF, 1: ON | Output 5 |  |  | Read/Write | 6304 | 25348 | 1 | 1 | 1 | M4M 20 I/O; M4M 30 I/O | Data Reading - I/O
| 0: OFF, 1: ON | Output 6 |  |  | Read/Write | 6305 | 25349 | 1 | 1 | 1 | M4M 20 I/O; M4M 30 I/O | Data Reading - I/O
Inputs | 0: OFF, 1: ON | Input 1 |  |  | Read | 6308 | 25352 | 1 | 1 | 1 | M4M 30 (all versions) | Data Reading - I/O
| 0: OFF, 1: ON | Input 2 |  |  | Read | 6309 | 25353 | 1 | 1 | 1 | M4M 30 (all versions) | Data Reading - I/O
| 0: OFF, 1: ON | Input 3 |  |  | Read | 630A | 25354 | 1 | 1 | 1 | M4M 30 (all versions) | Data Reading - I/O
| 0: OFF, 1: ON | Input 4 |  |  | Read | 630B | 25355 | 1 | 1 | 1 | M4M 30 (all versions) | Data Reading - I/O
| 0: OFF, 1: ON | Input 5 |  |  | Read | 630C | 25356 | 1 | 1 | 1 | M4M 20 I/O; M4M 30 I/O | Data Reading - I/O
| 0: OFF, 1: ON | Input 6 |  |  | Read | 630D | 25357 | 1 | 1 | 1 | M4M 20 I/O; M4M 30 I/O | Data Reading - I/O
Inputs Counter |  | Input Counter 1 |  |  | Read | 6318 | 25368 | 1 | 4 | 4 | M4M 30 (all versions) | Data Reading - I/O
|  | Input Counter 2 |  |  | Read | 631C | 25372 | 1 | 4 | 4 | M4M 30 (all versions) | Data Reading - I/O
|  | Input Counter 3 |  |  | Read | 6320 | 25376 | 1 | 4 | 4 | M4M 30 (all versions) | Data Reading - I/O
|  | Input Counter 4 |  |  | Read | 6324 | 25380 | 1 | 4 | 4 | M4M 30 (all versions) | Data Reading - I/O
|  | Input Counter 5 |  |  | Read | 6328 | 25384 | 1 | 4 | 4 | M4M 20 I/O; M4M 30 I/O | Data Reading - I/O
|  | Input Counter 6 |  |  | Read | 632C | 25388 | 1 | 4 | 4 | M4M 20 I/O; M4M 30 I/O | Data Reading - I/O
Analogue Outputs |  | Analogue Output 1 |  |  | Read | 6338 | 25400 | 1 | 4 | 4 | M4M 20 I/O; M4M 30 I/O | Data Reading - I/O
|  | Analogue Output 2 |  |  | Read | 6339 | 25401 | 1 | 4 | 4 | M4M 20 I/O; M4M 30 I/O | Data Reading - I/O
Errors Log |  | Header - Get next entry |  | Unsigned | Write | 6500 | 25856 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Notifications
|  | Header - Entry Number |  | Unsigned | Read/Write | 6501 | 25857 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Notifications
|  | Header - Direction |  | Unsigned | Read/Write | 6507 | 25863 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Notifications
|  | Data block |  |  | Read | 6510 | 25872 | 1 | 105 | 105 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Notifications
Alarms log |  | Header - Get next entry |  | Unsigned | Write | 65B0 | 26032 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Notifications
|  | Header - Entry Number |  | Unsigned | Read/Write | 65B1 | 26033 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Notifications
|  | Header - Direction |  | Unsigned | Read/Write | 65B7 | 26039 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Notifications
|  | Data block |  |  | Read | 65C0 | 26048 | 1 | 105 | 105 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Notifications
Audit Log |  | Header - Get next entry |  | Unsigned | Write | 6660 | 26208 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Notifications
|  | Header - Entry Number |  | Unsigned | Read/Write | 6661 | 26209 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Notifications
|  | Header - Direction |  | Unsigned | Read/Write | 6667 | 26215 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Notifications
|  | Data block - Entry_Num |  | Unsigned | Read | 6670 | 26224 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Notifications
|  | Data block - Timestamp (seconds from 2010-01-01 |  | Unsigned | Read | 6672 | 26226 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Notifications
|  | Data block - Upgrade_Counter |  | Unsigned | Read | 6674 | 26228 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Notifications
|  | Data block - FW_Version |  | ASCII | Read | 6675 | 26229 | 1 | 6 | 6 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Notifications
|  | Data block - TRAFO_V_Prim |  | Unsigned | Read | 667B | 26235 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Notifications
|  | Data block - TRAFO_V_Sec |  | Unsigned | Read | 667D | 26237 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Notifications
|  | Data block - TRAFO_I_Prim |  | Unsigned | Read | 667F | 26239 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Notifications
|  | Data block - TRAFO_I_Sec |  | Unsigned | Read | 6681 | 26241 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Notifications
|  | Data block - TRAFO_IN_Prim |  | Unsigned | Read | 6683 | 26243 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Notifications
|  | Data block - TRAFO_IN_Sec |  | Unsigned | Read | 6685 | 26245 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Notifications
|  | Data block - WIRES |  | Unsigned | Read | 6687 | 26247 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Notifications
|  | Data block - ACTIVE_ENERGY_IMPORT_TOTAL | 0.001 | Unsigned | Read | 6688 | 26248 | 1 | 4 | 4 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Notifications
|  | Data block - ACTIVE_ENERGY_IMPORT_L1 | 0.001 | Unsigned | Read | 668C | 26252 | 1 | 4 | 4 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Notifications
|  | Data block - ACTIVE_ENERGY_IMPORT_L2 | 0.001 | Unsigned | Read | 6690 | 26256 | 1 | 4 | 4 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Notifications
|  | Data block - ACTIVE_ENERGY_IMPORT_L3 | 0.001 | Unsigned | Read | 6694 | 26260 | 1 | 4 | 4 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Notifications
|  | Data block - ACTIVE_ENERGY_IMPORT_TAR1 | 0.001 | Unsigned | Read | 6698 | 26264 | 1 | 4 | 4 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Notifications
|  | Data block - ACTIVE_ENERGY_IMPORT_TAR2 | 0.001 | Unsigned | Read | 669C | 26268 | 1 | 4 | 4 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Notifications
|  | Data block - ACTIVE_ENERGY_IMPORT_TAR3 | 0.001 | Unsigned | Read | 66A0 | 26272 | 1 | 4 | 4 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Notifications
|  | Data block - ACTIVE_ENERGY_IMPORT_TAR4 | 0.001 | Unsigned | Read | 66A4 | 26276 | 1 | 4 | 4 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Notifications
|  | Data block - ACTIVE_ENERGY_IMPORT_TAR5 | 0.001 | Unsigned | Read | 66A8 | 26280 | 1 | 4 | 4 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Notifications
|  | Data block - ACTIVE_ENERGY_IMPORT_TAR6 | 0.001 | Unsigned | Read | 66AC | 26284 | 1 | 4 | 4 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Notifications
|  | Data block - ACTIVE_ENERGY_EXPORT_TOTAL | 0.001 | Unsigned | Read | 66B0 | 26288 | 1 | 4 | 4 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Notifications
Warnings log |  | Header - Get next entry |  | Unsigned | Write | 6710 | 26384 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Notifications
|  | Header - Entry Number |  | Unsigned | Read/Write | 6711 | 26385 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Notifications
|  | Header - Direction |  | Unsigned | Read/Write | 6717 | 26391 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Notifications
|  | Data block |  |  | Read | 6720 | 26400 | 1 | 105 | 105 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Notifications
Energy Cumulative |  | Header - Get next entry |  |  | Read/Write | 8000 | 32768 |  | 1 | 1 | M4M 30 (all versions) | Data Reading - Historicals
|  | Header - Entry Number |  |  | Read/Write | 8001 | 32769 |  | 1 | 1 | M4M 30 (all versions) | Data Reading - Historicals
|  | Header - Date Time |  |  | Read/Write | 8004 | 32772 |  | 3 | 3 | M4M 30 (all versions) | Data Reading - Historicals
|  | Header - Direction |  |  | Read/Write | 8007 | 32775 |  | 1 | 1 | M4M 30 (all versions) | Data Reading - Historicals
|  | Data block 1 |  |  | Read | 8010 | 32784 |  | 83 | 83 | M4M 30 (all versions) | Data Reading - Historicals
|  | Data block 2 |  |  | Read | 8070 | 32880 |  | 83 | 83 | M4M 30 (all versions) | Data Reading - Historicals
|  | Data block 3 |  |  | Read | 80D0 | 32976 |  | 83 | 83 | M4M 30 (all versions) | Data Reading - Historicals
|  | Data block 4 |  |  | Read | 8130 | 33072 |  | 83 | 83 | M4M 30 (all versions) | Data Reading - Historicals
|  | Data block 5 |  |  | Read | 8190 | 33168 |  | 83 | 83 | M4M 30 (all versions) | Data Reading - Historicals
|  | Data block 6 |  |  | Read | 81F0 | 33264 |  | 83 | 83 | M4M 30 (all versions) | Data Reading - Historicals
|  | Data block 7 |  |  | Read | 8250 | 33360 |  | 83 | 83 | M4M 30 (all versions) | Data Reading - Historicals
Energy Snapshots |  | Header - Get next entry |  |  | Read/Write | 8300 | 33536 |  | 1 | 1 | M4M 30 (all versions) | Data Reading - Historicals
|  | Header - Entry Number |  |  | Read/Write | 8301 | 33537 |  | 1 | 1 | M4M 30 (all versions) | Data Reading - Historicals
|  | Header - Date Time |  |  | Read/Write | 8304 | 33540 |  | 3 | 3 | M4M 30 (all versions) | Data Reading - Historicals
|  | Header - Direction |  |  | Read/Write | 8307 | 33543 |  | 1 | 1 | M4M 30 (all versions) | Data Reading - Historicals
|  | Data block 1 |  |  | Read | 8310 | 33552 |  | 83 | 83 | M4M 30 (all versions) | Data Reading - Historicals
|  | Data block 2 |  |  | Read | 8370 | 33648 |  | 83 | 83 | M4M 30 (all versions) | Data Reading - Historicals
|  | Data block 3 |  |  | Read | 83D0 | 33744 |  | 83 | 83 | M4M 30 (all versions) | Data Reading - Historicals
|  | Data block 4 |  |  | Read | 8430 | 33840 |  | 83 | 83 | M4M 30 (all versions) | Data Reading - Historicals
|  | Data block 5 |  |  | Read | 8490 | 33936 |  | 83 | 83 | M4M 30 (all versions) | Data Reading - Historicals
|  | Data block 6 |  |  | Read | 84F0 | 34032 |  | 83 | 83 | M4M 30 (all versions) | Data Reading - Historicals
|  | Data block 7 |  |  | Read | 8550 | 34128 |  | 83 | 83 | M4M 30 (all versions) | Data Reading - Historicals
Load profile |  | Header - Get next block |  |  | Read/Write | 8700 | 34560 |  | 1 | 1 | M4M 30 (all versions) | Data Reading - Historicals
|  | Header - Channel number |  |  | Read/Write | 8703 | 34563 |  | 1 | 1 | M4M 30 (all versions) | Data Reading - Historicals
|  | Header - Date / Time |  |  | Read/Write | 8704 | 34564 |  | 3 | 3 | M4M 30 (all versions) | Data Reading - Historicals
|  | Header - Direction |  |  | Read/Write | 8707 | 34567 |  | 1 | 1 | M4M 30 (all versions) | Data Reading - Historicals
|  | Channel information - quantity |  |  | Read/Write | 8710 | 34576 |  | 3 | 3 | M4M 30 (all versions) | Data Reading - Historicals
|  | Channel information - scaler |  |  | Read/Write | 8713 | 34579 |  | 1 | 1 | M4M 30 (all versions) | Data Reading - Historicals
|  | Channel information - interval |  |  | Read/Write | 8714 | 34580 |  | 2 | 2 | M4M 30 (all versions) | Data Reading - Historicals
|  | Channel information - datatype |  |  | Read/Write | 8716 | 34582 |  | 1 | 1 | M4M 30 (all versions) | Data Reading - Historicals
|  | Data block |  |  | Read | 8720 | 34592 |  | 120 | 120 | M4M 30 (all versions) | Data Reading - Historicals
Serial number(s) |  |  |  | ASCII | Read | 8900 | 35072 | 1 | 5 | 5 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - Device info
Meter firmware version |  |  |  | ASCII | Read | 8908 | 35080 | 1 | 8 | 8 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - Device info
Product type number ID |  | See Details sheet |  |  | Read | 8910 | 35088 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - Device info
Slave ID |  |  |  |  | Read | 8911 | 35089 | 1 | 8 | 8 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - Device info
Product tag name |  |  |  | ASCII | Read/Write | 8919 | 35097 | 1 | 5 | 5 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - Device info
Type designation |  | E.g. M4M30SMA |  | ASCII | Read | 8960 | 35168 | 1 | 6 | 6 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - Device info
Product Name |  | E.g. M4M 30 MODBUS |  | ASCII | Read | 8966 | 35174 | 1 | 8 | 8 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - Device info
Date Time |  | YYMMDD:HHMMSS |  |  | Read/Write | 8A00 | 35328 | 1 | 3 | 3 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - Date and Time
Day of week |  |  |  |  | Read | 8A03 | 35331 | 1 | 2 | 2 | M4M 30 (all versions) | Configuration - Tariffs
Active day type |  | Read only |  |  | Read | 8A05 | 35333 | 1 | 1 | 1 | M4M 30 (all versions) | Configuration - Tariffs
Active season |  | Read only |  |  | Read | 8A06 | 35334 | 1 | 1 | 1 | M4M 30 (all versions) | Configuration - Tariffs
Current tariff |  | Current active tariff (form 1 to 6) |  | Unsigned | Read/Write | 8A07 | 35335 | 1 | 1 | 1 | M4M 30 (all versions) | Configuration - Tariffs
Error flags |  | 64 bits flags |  |  | Read only | 8A13 | 35347 | 1 | 4 | 4 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Notifications
Information flags | 25 Alarm flags | 64 bits flags |  |  | Read only | 8A19 | 35353 | 1 | 4 | 4 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Notifications
Warning flags |  | 64 bits flags |  |  | Read only | 8A1F | 35359 | 1 | 4 | 4 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Notifications
Alarm flags (simple and complex) |  | 64 bits flags (25 Alarm flags used) |  |  | Read only | 8A25 | 35365 | 1 | 4 | 4 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Alarms
Transformer ratios |  | CT L1,L2,L3 ratio (Numerator) |  | Unsigned | Read/Write | 8C00 | 35840 | 1 | 2 | 2 | M4M 20 (all versions except M4M 20 Rogowski); M4M 30 (all versions except M4M 30 Rogowski) | Configuration - Installation
|  | CT L1,L2,L3 ratio (Denominator) |  | Unsigned | Read/Write | 8C02 | 35842 | 1 | 2 | 2 | M4M 20 (all versions except M4M 20 Rogowski); M4M 30 (all versions except M4M 30 Rogowski) | Configuration - Installation
|  | VT ratio (Numerator) |  | Unsigned | Read/Write | 8C04 | 35844 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - Installation
|  | VT ratio (Denominator) |  | Unsigned | Read/Write | 8C06 | 35846 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - Installation
|  | CT Neutral ratio (Numerator) |  | Unsigned | Read/Write | 8C08 | 35848 | 1 | 2 | 2 | M4M 30 (all versions except M4M 30 Rogowski) | Configuration - Installation
|  | CT Neutral ratio (Denominator) |  | Unsigned | Read/Write | 8C0A | 35850 | 1 | 2 | 2 | M4M 30 (all versions except M4M 30 Rogowski) | Configuration - Installation
I/O settings |  | I/O port 1 |  |  | Read/Write | 8C0C | 35852 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - I/O
|  | I/O port 2 |  |  | Read/Write | 8C0D | 35853 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - I/O
|  | I/O port 3 |  |  | Read/Write | 8C0E | 35854 | 1 | 1 | 1 | M4M 30 (all versions) | Configuration - I/O
|  | I/O port 4 |  |  | Read/Write | 8C0F | 35855 | 1 | 1 | 1 | M4M 30 (all versions) | Configuration - I/O
|  | I/O port 5 |  |  | Read/Write | 8C10 | 35856 | 1 | 1 | 1 | M4M 20 I/O; M4M 30 I/O | Configuration - I/O
|  | I/O port 6 |  |  | Read/Write | 8C11 | 35857 | 1 | 1 | 1 | M4M 20 I/O; M4M 30 I/O | Configuration - I/O
I/O settings - Pulse outputs configuration |  | Pulse output instance |  |  | Read/Write | 8C12 | 35858 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - I/O
|  | Port number |  |  | Read/Write | 8C13 | 35859 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - I/O
| OBIS code | Energy parameter |  |  | Read/Write | 8C14 | 35860 | 1 | 3 | 3 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - I/O
| kWh | Pulse frequency active energy |  |  | Read/Write | 8C17 | 35863 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - I/O
| kvarh | Pulse frequency reactive energy |  |  | Read/Write | 8C19 | 35865 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - I/O
| milliseconds | Pulse length |  |  | Read/Write | 8C1B | 35867 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - I/O
|  | Turn off pulse output |  |  | Read/Write | 8C1D | 35869 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - I/O
Load profile settings |  | Channel number |  |  | Read/Write | 8C20 | 35872 | 1 | 1 | 1 | M4M 30 (all versions) | Configuration - Historicals
| OBIS code | Parameter |  |  | Read/Write | 8C21 | 35873 | 1 | 3 | 3 | M4M 30 (all versions) | Configuration - Historicals
| minutes | Interval |  |  | Read/Write | 8C24 | 35876 | 1 | 2 | 2 | M4M 30 (all versions) | Configuration - Historicals
|  | Max number of snapshot |  |  | Read/Write | 8C26 | 35878 | 1 | 2 | 2 | M4M 30 (all versions) | Configuration - Historicals
Max/Min Demand settings |  | Number of quantities |  |  | Read/Write | 8C30 | 35888 | 1 | 1 | 1 | M4M 30 (all versions) | Configuration - Historicals
|  | Parameter number |  |  | Read | 8C31 | 35889 | 1 | 1 | 1 | M4M 30 (all versions) | Configuration - Historicals
| OBIS code | Parameter |  |  | Read/Write | 8C32 | 35890 | 1 | 3 | 3 | M4M 30 (all versions) | Configuration - Historicals
| OBIS code | Level of Min/Max |  |  | Read/Write | 8C35 | 35893 | 1 | 3 | 3 | M4M 30 (all versions) | Configuration - Historicals
|  | Number of levels |  |  | Read/Write | 8C38 | 35896 | 1 | 1 | 1 | M4M 30 (all versions) | Configuration - Historicals
| minutes | Interval |  |  | Read/Write | 8C39 | 35897 | 1 | 1 | 1 | M4M 30 (all versions) | Configuration - Historicals
| minutes | Sub interval |  |  | Read/Write | 8C3A | 35898 | 1 | 1 | 1 | M4M 30 (all versions) | Configuration - Historicals
|  | Period |  |  | Read/Write | 8C3B | 35899 | 1 | 1 | 1 | M4M 30 (all versions) | Configuration - Historicals
Energy Cumulative/Snapshots settings |  | Number of channel |  |  | Read/Write | 8C50 | 35920 | 1 | 1 | 1 | M4M 30 (all versions) | Configuration - Historicals
|  | Channel number |  |  | Read | 8C51 | 35921 | 1 | 1 | 1 | M4M 30 (all versions) | Configuration - Historicals
| OBIS code | Quantity |  |  | Read/Write | 8C52 | 35922 | 1 | 3 | 3 | M4M 30 (all versions) | Configuration - Historicals
|  | Period |  |  | Read/Write | 8C55 | 35925 | 1 | 1 | 1 | M4M 30 (all versions) | Configuration - Historicals
Alarm settings |  | Channel alarm number |  |  | Read/Write | 8C60 | 35936 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - Alarms
| OBIS code | Quantity |  |  | Read/Write | 8C61 | 35937 | 1 | 3 | 3 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - Alarms
|  | Threshold |  |  | Read/Write | 8C64 | 35940 | 1 | 4 | 4 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - Alarms
| % | Hysteresis |  |  | Read/Write | 8C68 | 35944 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - Alarms
| seconds | Delays |  |  | Read/Write | 8C69 | 35945 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - Alarms
|  | Type of alarm |  |  | Read/Write | 8C6B | 35947 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - Alarms
|  | Action - alarm triggered |  |  | Read/Write | 8C6C | 35948 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - Alarms
Complex Alarms |  | Channel complex alarm number |  |  | Read/Write | 8C80 | 35968 | 1 | 1 | 1 | M4M 30 (all versions) | Configuration - Complex alarms
|  | Components |  |  | Read/Write | 8C81 | 35969 | 4 | 1 | 4 | M4M 30 (all versions) | Configuration - Complex alarms
|  | Operators |  |  | Read/Write | 8C85 | 35973 | 1 | 1 | 1 | M4M 30 (all versions) | Configuration - Complex alarms
|  | Action - complex alarm triggered |  |  | Read/Write | 8C86 | 35974 | 1 | 2 | 2 | M4M 30 (all versions) | Configuration - Complex alarms
Tariff settings |  | Tariffs source |  |  | Read/Write | 8C90 | 35984 | 1 | 1 | 1 | M4M 30 (all versions) | Configuration - Tariffs
|  | Input configuration |  |  | Read/Write | 8C91 | 35985 | 1 | 1 | 1 | M4M 30 (all versions) | Configuration - Tariffs
|  | Number of day profile |  |  | Read/Write | 8CCD | 36045 | 1 | 1 | 1 | M4M 30 (all versions) | Configuration - Tariffs
|  | Day profile number |  |  | Read | 8CCE | 36046 | 1 | 1 | 1 | M4M 30 (all versions) | Configuration - Tariffs
|  | Number of actions |  |  | Read/Write | 8CCF | 36047 | 1 | 1 | 1 | M4M 30 (all versions) | Configuration - Tariffs
|  | Action number |  |  | Read | 8CD0 | 36048 | 1 | 1 | 1 | M4M 30 (all versions) | Configuration - Tariffs
|  | Action (time, action) |  |  | Read/Write | 8CD1 | 36049 | 1 | 2 | 2 | M4M 30 (all versions) | Configuration - Tariffs
CO2 conversion factor actIive energy | kg / kWh | Range: 0.001 - 9.999 |  | Unsigned | Read/Write | 8CE0 | 36064 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - Energy Conversion
Currency conversion factor active enenrgy | Currency / kWh | Range: 0.001 - 999999.000 |  | Unsigned | Read/Write | 8CE2 | 36066 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - Energy Conversion
LED source |  | 0 = Active energy, 1 = Reactive energy |  |  | Read/Write | 8CE4 | 36068 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - I/O
Wires |  | See Details sheet |  | Unsigned | Read/Write | 8CE5 | 36069 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - Installation
DST start |  | month, day of month, day of week, hour |  |  | Read/Write | 8CE6 | 36070 | 1 | 2 | 2 | M4M 30 (all versions) | Configuration - Tariffs
DST end |  | month, day of month, day of week, hour |  |  | Read/Write | 8CE8 | 36072 | 1 | 2 | 2 | M4M 30 (all versions) | Configuration - Tariffs
DST enabled |  | 0 = disabled, 1 = enabled |  |  | Read/Write | 8CEA | 36074 | 1 | 1 | 1 | M4M 30 (all versions) | Configuration - Tariffs
Modbus RTU |  | Address: 1 - 247 |  | Unsigned | Read/Write | 8CEB | 36075 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - Communication
|  | Baudrate: 9600, 19200, 38400, 57600, 115200 |  | Unsigned | Read/Write | 8CEC | 36076 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - Communication
|  | Parity: 2- none; 1-even; 0- odd |  | Unsigned | Read/Write | 8CEE | 36078 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - Communication
Modbus TCP/IP |  | DHCP: 0-disable; 1- enable |  | Unsigned | Read/Write | 8CEF | 36079 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - Communication
|  | IP: A.B.C.D -> 0xAABBCCDD |  | Unsigned | Read/Write | 8CF0 | 36080 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - Communication
|  | Mask: A.B.C.D -> 0xAABBCCDD |  | Unsigned | Read/Write | 8CF2 | 36082 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - Communication
|  | Gateway: A.B.C.D -> 0xAABBCCDD |  | Unsigned | Read/Write | 8CF4 | 36084 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - Communication
|  | TCP Port: 502(default), 0xFFFF (max value) |  | Unsigned | Read/Write | 8CF6 | 36086 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - Communication
Up/Down Counters |  | Up Counter |  | Unsigned | Read | 8CF7 | 36087 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Timers
|  | Down Counter |  | Unsigned | Read | 8CF9 | 36089 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Timers
|  | Down Counter Reset Value |  | Unsigned | Read/Write | 8CFB | 36091 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - Timers
HMI Config |  | Brightness (range: 0 - 255) |  | Unsigned | Read/Write | 8CFD | 36093 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - Unit
|  | Language (range: 0-max language number) |  | Unsigned | Read/Write | 8CFE | 36094 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - Unit
Reset Logs |  | Write 1 to perform the reset |  | Unsigned | Write | 8F57 | 36695 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - Reset
Reset historical functionality |  | Write 1 to perform the reset |  | Unsigned | Write | 8F58 | 36696 | 1 | 1 | 1 | M4M 30 (all versions) | Configuration - Reset
Reset Timer |  | Write 1 to perform the reset |  | Unsigned | Write | 8F59 | 36697 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - Reset
Reset Energy |  | Write 1 to perform the reset |  | Unsigned | Write | 8F5A | 36698 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - Reset
Reset Factory setting default |  | Write 1 to perform the reset |  | Unsigned | Write | 8F5B | 36699 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - Reset
Reset Max / Min / Average |  | Write 1 to perform the reset |  | Unsigned | Write | 8F5C | 36700 | 1 | 1 | 1 | M4M 20 (all versions); M4M 30 (all versions) | Configuration - Reset
Max/Min Demand |  | Header - Get next entry |  |  | Read/Write | 8F72 | 36722 |  | 1 | 1 | M4M 30 (all versions) | Configuration - Historicals
|  | Header - Entry number |  |  | Read/Write | 8F73 | 36723 |  | 1 | 1 | M4M 30 (all versions) | Configuration - Historicals
|  | Header - Date / time |  |  | Read/Write | 8F76 | 36726 |  | 3 | 3 | M4M 30 (all versions) | Configuration - Historicals
|  | Header - Direction |  |  | Read/Write | 8F79 | 36729 |  | 1 | 1 | M4M 30 (all versions) | Configuration - Historicals
|  | Data Block 1 |  |  | Read | 8F82 | 36738 |  | 115 | 115 | M4M 30 (all versions) | Configuration - Historicals
|  | Data Block 2 |  |  | Read | 9002 | 36866 |  | 115 | 115 | M4M 30 (all versions) | Configuration - Historicals
|  | Data Block 3 |  |  | Read | 9082 | 36994 |  | 115 | 115 | M4M 30 (all versions) | Configuration - Historicals
|  | Data Block 4 |  |  | Read | 9102 | 37122 |  | 115 | 115 | M4M 30 (all versions) | Configuration - Historicals
|  | Data Block 5 |  |  | Read | 9182 | 37250 |  | 115 | 115 | M4M 30 (all versions) | Configuration - Historicals
|  | Data Block 6 |  |  | Read | 9202 | 37378 |  | 115 | 115 | M4M 30 (all versions) | Configuration - Historicals
|  | Data Block 7 |  |  | Read | 9282 | 37506 |  | 115 | 115 | M4M 30 (all versions) | Configuration - Historicals
|  | Data Block 8 |  |  | Read | 9302 | 37634 |  | 115 | 115 | M4M 30 (all versions) | Configuration - Historicals
|  | Data Block 9 |  |  | Read | 9382 | 37762 |  | 115 | 115 | M4M 30 (all versions) | Configuration - Historicals
|  | Data Block 10 |  |  | Read | 9402 | 37890 |  | 115 | 115 | M4M 30 (all versions) | Configuration - Historicals
|  | Data Block 11 |  |  | Read | 9482 | 38018 |  | 115 | 115 | M4M 30 (all versions) | Configuration - Historicals
|  | Data Block 12 |  |  | Read | 9502 | 38146 |  | 115 | 115 | M4M 30 (all versions) | Configuration - Historicals
|  | Data Block 13 |  |  | Read | 9582 | 38274 |  | 115 | 115 | M4M 30 (all versions) | Configuration - Historicals
|  | Data Block 14 |  |  | Read | 9602 | 38402 |  | 115 | 115 | M4M 30 (all versions) | Configuration - Historicals
|  | Data Block 15 |  |  | Read | 9682 | 38530 |  | 115 | 115 | M4M 30 (all versions) | Configuration - Historicals
|  | Data Block 16 |  |  | Read | 9702 | 38658 |  | 115 | 115 | M4M 30 (all versions) | Configuration - Historicals
|  | Data Block 17 |  |  | Read | 9782 | 38786 |  | 115 | 115 | M4M 30 (all versions) | Configuration - Historicals
|  | Data Block 18 |  |  | Read | 9802 | 38914 |  | 115 | 115 | M4M 30 (all versions) | Configuration - Historicals
|  | Data Block 19 |  |  | Read | 9882 | 39042 |  | 115 | 115 | M4M 30 (all versions) | Configuration - Historicals
Active power total Scaler 1 | W | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CB1A | 51994 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Active power L1 Scaler 1 | W | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CB1C | 51996 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Active power L2 Scaler 1 | W | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CB1E | 51998 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Active power L3 Scaler 1 | W | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CB20 | 52000 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Reactive power total Scaler 1 | VAR | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CB22 | 52002 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Reactive power L1 Scaler 1 | VAR | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CB24 | 52004 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Reactive power L2 Scaler 1 | VAR | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CB26 | 52006 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Reactive power L3 Scaler 1 | VAR | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CB28 | 52008 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Apparent power total Scaler 1 | VA | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CB2A | 52010 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Apparent power L1 Scaler 1 | VA | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CB2C | 52012 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Apparent power L2 Scaler 1 | VA | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CB2E | 52014 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Apparent power L3 Scaler 1 | VA | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CB30 | 52016 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Real-Time values
Average Active power total Scaler 1 | W | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CBE8 | 52200 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Average Active power L1 Scaler 1 | W | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CBEA | 52202 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Average Active power L2 Scaler 1 | W | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CBEC | 52204 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Average Active power L3 Scaler 1 | W | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CBEE | 52206 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Average Reactive power total Scaler 1 | VAR | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CBF0 | 52208 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Average Reactive power L1 Scaler 1 | VAR | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CBF2 | 52210 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Average Reactive power L2 Scaler 1 | VAR | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CBF4 | 52212 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Average Reactive power L3 Scaler 1 | VAR | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CBF6 | 52214 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Average Apparent power total Scaler 1 | VA | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CBF8 | 52216 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Average Apparent power L1 Scaler 1 | VA | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CBFA | 52218 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Average Apparent power L2 Scaler 1 | VA | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CBFC | 52220 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Average Apparent power L3 Scaler 1 | VA | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CBFE | 52222 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Max Active power total Scaler 1 | W | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CC24 | 52260 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Max Active power L1 Scaler 1 | W | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CC26 | 52262 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Max Active power L2 Scaler 1 | W | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CC28 | 52264 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Max Active power L3 Scaler 1 | W | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CC2A | 52266 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Max Reactive power total Scaler 1 | VAR | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CC2C | 52268 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Max Reactive power L1 Scaler 1 | VAR | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CC2E | 52270 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Max Reactive power L2 Scaler 1 | VAR | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CC30 | 52272 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Max Reactive power L3 Scaler 1 | VAR | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CC32 | 52274 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Max Apparent power total Scaler 1 | VA | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CC34 | 52276 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Max Apparent power L1 Scaler 1 | VA | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CC36 | 52278 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Max Apparent power L2 Scaler 1 | VA | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CC38 | 52280 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Max Apparent power L3 Scaler 1 | VA | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CC3A | 52282 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Min Active power total Scaler 1 | W | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CC9C | 52380 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Min Active power L1 Scaler 1 | W | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CC9E | 52382 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Min Active power L2 Scaler 1 | W | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CCA0 | 52384 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Min Active power L3 Scaler 1 | W | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CCA2 | 52386 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Min Reactive power total Scaler 1 | VAR | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CCA4 | 52388 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Min Reactive power L1 Scaler 1 | VAR | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CCA6 | 52390 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Min Reactive power L2 Scaler 1 | VAR | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CCA8 | 52392 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Min Reactive power L3 Scaler 1 | VAR | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CCAA | 52394 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Min Apparent power total Scaler 1 | VA | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CCAC | 52396 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Min Apparent power L1 Scaler 1 | VA | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CCAE | 52398 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Min Apparent power L2 Scaler 1 | VA | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CCB0 | 52400 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values
Min Apparent power L3 Scaler 1 | VA | Data value - available from FW version P1.3.10.0 | 1 | Signed | Read | CCB2 | 52402 | 1 | 2 | 2 | M4M 20 (all versions); M4M 30 (all versions) | Data Reading - Avg/Min/Max values

## M2M mapping table
Parameter | Unit | Details | Resolution | Data Type | Access | Register (Hex) | Reg (Dec) | Nr of quantities | Size | Nr of registers | Product Type
3-PHASE SYSTEM VOLTAGE | Volt | Compatible with M2M mapping | 1 | Unsigned Long | Read | 1000 | 4096 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
PHASE VOLTAGE L1-N | Volt | Compatible with M2M mapping | 1 | Unsigned Long | Read | 1002 | 4098 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
PHASE VOLTAGE L2-N | Volt | Compatible with M2M mapping | 1 | Unsigned Long | Read | 1004 | 4100 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
PHASE VOLTAGE L3-N | Volt | Compatible with M2M mapping | 1 | Unsigned Long | Read | 1006 | 4102 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
LINE VOLTAGE L1-2 | Volt | Compatible with M2M mapping | 1 | Unsigned Long | Read | 1008 | 4104 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
LINE VOLTAGE L2-3 | Volt | Compatible with M2M mapping | 1 | Unsigned Long | Read | 100A | 4106 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
LINE VOLTAGE L3-1 | Volt | Compatible with M2M mapping | 1 | Unsigned Long | Read | 100C | 4108 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
3-PHASE SYSTEM CURRENT | mA | Compatible with M2M mapping | 1 | Unsigned Long | Read | 100E | 4110 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
LINE CURRENT L1 | mA | Compatible with M2M mapping | 1 | Unsigned Long | Read | 1010 | 4112 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
LINE CURRENT L2 | mA | Compatible with M2M mapping | 1 | Unsigned Long | Read | 1012 | 4114 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
LINE CURRENT L3 | mA | Compatible with M2M mapping | 1 | Unsigned Long | Read | 1014 | 4116 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
3-PHASE SYS. POWER FACTOR I |  | Compatible with M2M mapping | 0.001 | Signed Long | Read | 1016 | 4118 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
POWER FACTOR L1 |  | Compatible with M2M mapping | 0.001 | Signed Long | Read | 1018 | 4120 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
POWER FACTOR L2 |  | Compatible with M2M mapping | 0.001 | Signed Long | Read | 101A | 4122 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
POWER FACTOR L3 |  | Compatible with M2M mapping | 0.001 | Signed Long | Read | 101C | 4124 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
3-PHASE SYSTEM COS ϕ |  | Compatible with M2M mapping | 0.001 | Signed Long | Read | 101E | 4126 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
PHASE COS ϕ1 |  | Compatible with M2M mapping | 0.001 | Signed Long | Read | 1020 | 4128 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
PHASE COS ϕ2 |  | Compatible with M2M mapping | 0.001 | Signed Long | Read | 1022 | 4130 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
PHASE COS ϕ3 |  | Compatible with M2M mapping | 0.001 | Signed Long | Read | 1024 | 4132 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
3-PHASE S. APPARENT POWER | VA | Compatible with M2M mapping | 1 | Unsigned Long | Read | 1026 | 4134 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
APPARENT POWER L1 | VA | Compatible with M2M mapping | 1 | Unsigned Long | Read | 1028 | 4136 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
APPARENT POWER L2 | VA | Compatible with M2M mapping | 1 | Unsigned Long | Read | 102A | 4138 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
APPARENT POWER L3 | VA | Compatible with M2M mapping | 1 | Unsigned Long | Read | 102C | 4140 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
3-PHASE SYS. ACTIVE POWER | Watt | Compatible with M2M mapping | 1 | Signed Long ( S ) | Read | 102E | 4142 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
ACTIVE POWER L1 | Watt | Compatible with M2M mapping | 1 | Signed Long ( S ) | Read | 1030 | 4144 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
ACTIVE POWER L2 | Watt | Compatible with M2M mapping | 1 | Signed Long ( S ) | Read | 1032 | 4146 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
ACTIVE POWER L3 | Watt | Compatible with M2M mapping | 1 | Signed Long ( S ) | Read | 1034 | 4148 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
3-PHASE S. REACTIVE POWER | VAr | Compatible with M2M mapping | 1 | Signed Long ( S ) | Read | 1036 | 4150 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
REACTIVE POWER L1 | VAr | Compatible with M2M mapping | 1 | Signed Long ( S ) | Read | 1038 | 4152 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
REACTIVE POWER L2 | VAr | Compatible with M2M mapping | 1 | Signed Long ( S ) | Read | 103A | 4154 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
REACTIVE POWER L3 | VAr | Compatible with M2M mapping | 1 | Signed Long ( S ) | Read | 103C | 4156 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
3-PHASE SYS. ACTIVE ENERGY | Wh | Compatible with M2M mapping | 100 | Unsigned Long | Read | 103E | 4158 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
3-PHASE S. REACTIVE ENERGY | VArh | Compatible with M2M mapping | 100 | Unsigned Long | Read | 1040 | 4160 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
FREQUENCY | mHz | Compatible with M2M mapping | 1 | Unsigned Long | Read | 1046 | 4166 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
MAX LINE CURRENT L1 | mA | Compatible with M2M mapping | 1 | Unsigned Long | Read | 1060 | 4192 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
MAX LINE CURRENT L2 | mA | Compatible with M2M mapping | 1 | Unsigned Long | Read | 1062 | 4194 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
MAX LINE CURRENT L3 | mA | Compatible with M2M mapping | 1 | Unsigned Long | Read | 1064 | 4196 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
MAX 3-PHASE SYS. ACTIVE POWER | Watt | Compatible with M2M mapping | 1 | Signed Long ( S ) | Read | 1066 | 4198 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
MAX 3-PHASE S. APPARENT POWER | VA | Compatible with M2M mapping | 1 | Unsigned Long | Read | 1068 | 4200 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
3-PHASE SYS. ACTIVE POWER 15’ AVER | Watt | Compatible with M2M mapping | 1 | Signed Long ( S ) | Read | 1070 | 4208 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
3-PHASE SYS. APPARENT POWER 15’ AVER | VA | Compatible with M2M mapping | 1 | Unsigned Long | Read | 1072 | 4210 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
ACTIVE ENERGY L1 | Wh | Compatible with M2M mapping | 100 | Unsigned Long | Read | 1074 | 4212 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
ACTIVE ENERGY L2 | Wh | Compatible with M2M mapping | 100 | Unsigned Long | Read | 1076 | 4214 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
ACTIVE ENERGY L3 | Wh | Compatible with M2M mapping | 100 | Unsigned Long | Read | 1078 | 4216 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
REACTIVE ENERGY L1 | VArh | Compatible with M2M mapping | 100 | Unsigned Long | Read | 107A | 4218 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
REACTIVE ENERGY L2 | VArh | Compatible with M2M mapping | 100 | Unsigned Long | Read | 107C | 4220 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
REACTIVE ENERGY L3 | VArh | Compatible with M2M mapping | 100 | Unsigned Long | Read | 107E | 4222 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
MAX 3-PHASE SYS. ACTIVE POWER 15’ AVER | Watt | Compatible with M2M mapping | 1 | Signed Long ( S ) | Read | 1080 | 4224 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
VOLTAGE THD L1 |  | Compatible with M2M mapping | 0.1 | Unsigned Long | Read | 1082 | 4226 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
VOLTAGE THD L2 |  | Compatible with M2M mapping | 0.1 | Unsigned Long | Read | 1084 | 4228 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
VOLTAGE THD L3 |  | Compatible with M2M mapping | 0.1 | Unsigned Long | Read | 1086 | 4230 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
CURRENT THD L1 |  | Compatible with M2M mapping | 0.1 | Unsigned Long | Read | 1088 | 4232 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
CURRENT THD L2 |  | Compatible with M2M mapping | 0.1 | Unsigned Long | Read | 108A | 4234 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
CURRENT THD L3 |  | Compatible with M2M mapping | 0.1 | Unsigned Long | Read | 108C | 4236 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
MAX ACTIVE POWER 15’ AVER L1 | Watt | Compatible with M2M mapping | 1 | Signed Long ( S ) | Read | 108E | 4238 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
MAX ACTIVE POWER 15’ AVER L2 | Watt | Compatible with M2M mapping | 1 | Signed Long ( S ) | Read | 1090 | 4240 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
MAX ACTIVE POWER 15’ AVER L3 | Watt | Compatible with M2M mapping | 1 | Signed Long ( S ) | Read | 1092 | 4242 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
MAX 3-PHASE SYS. APPARENT POWER 15’ AVER | VA | Compatible with M2M mapping | 1 | Unsigned Long | Read | 1094 | 4244 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
MAX APPARERENT POWER 15’ AVER L1 | VA | Compatible with M2M mapping | 1 | Unsigned Long | Read | 1096 | 4246 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
MAX APPARERENT POWER 15’ AVER L2 | VA | Compatible with M2M mapping | 1 | Unsigned Long | Read | 1098 | 4248 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
MAX APPARERENT POWER 15’ AVER L3 | VA | Compatible with M2M mapping | 1 | Unsigned Long | Read | 109A | 4250 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
3-PHASE SYS. APPARENT ENERGY | VAh | Compatible with M2M mapping | 100 | Unsigned Long | Read | 10A6 | 4262 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
APPARENT ENERGY L1 | VAh | Compatible with M2M mapping | 100 | Unsigned Long | Read | 10A8 | 4264 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
APPARENT ENERGY L2 | VAh | Compatible with M2M mapping | 100 | Unsigned Long | Read | 10AA | 4266 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
APPARENT ENERGY L3 | VAh | Compatible with M2M mapping | 100 | Unsigned Long | Read | 10AC | 4268 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
3-PHASE SYS. GENERATED ACTIVE ENERGY | Wh | Compatible with M2M mapping | 100 | Unsigned Long | Read | 10AE | 4270 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
GENERATED ACTIVE ENERGY L1 | Wh | Compatible with M2M mapping | 100 | Unsigned Long | Read | 10B0 | 4272 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
GENERATED ACTIVE ENERGY L2 | Wh | Compatible with M2M mapping | 100 | Unsigned Long | Read | 10B2 | 4274 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
GENERATED ACTIVE ENERGY L3 | Wh | Compatible with M2M mapping | 100 | Unsigned Long | Read | 10B4 | 4276 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
3-PHASE S. GENERATED REACTIVE ENERGY | VArh | Compatible with M2M mapping | 100 | Unsigned Long | Read | 10B6 | 4278 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
GENERATED REACTIVE ENERGY L1 | VArh | Compatible with M2M mapping | 100 | Unsigned Long | Read | 10B8 | 4280 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
GENERATED REACTIVE ENERGY L2 | VArh | Compatible with M2M mapping | 100 | Unsigned Long | Read | 10BA | 4282 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
GENERATED REACTIVE ENERGY L3 | VArh | Compatible with M2M mapping | 100 | Unsigned Long | Read | 10BC | 4284 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
3-PHASE S. GENERATED APPARENT ENERGY | VAh | Compatible with M2M mapping | 100 | Unsigned Long | Read | 10BE | 4286 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
GENERATED APPARENT ENERGY L1 | VAh | Compatible with M2M mapping | 100 | Unsigned Long | Read | 10C0 | 4288 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
GENERATED APPARENT ENERGY L2 | VAh | Compatible with M2M mapping | 100 | Unsigned Long | Read | 10C2 | 4290 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
GENERATED APPARENT ENERGY L3 | VAh | Compatible with M2M mapping | 100 | Unsigned Long | Read | 10C4 | 4292 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
CURRENT TRANSFORMER PRIMARY (CT) |  | Deviation vs M2M: it represents the CT Primary, not ratio | 1 | Unsigned Long | Read | 11A0 | 4512 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)
VOLTAGE TRANSFORMER PRIMARY (VT) |  | Deviation vs M2M: it represents the VT Primary, not ratio | 1 | Unsigned Long | Read | 11A2 | 4514 | 1 | 2 | 2 | M4M 20 (from FW P1.3.10.0); M4M 30 (from FW P1.3.10.0)

## OBIS Code
Parameter | OBIS Code | Column1 | Column2
TOTAL ENERGIES:
Active energy import total | 1.0.1.8.0.255
Active energy export total | 1.0.2.8.0.255
Active energy net total | 1.0.16.8.0.255
Reactive energy import total | 1.0.3.8.0.255
Reactive energy export total | 1.0.4.8.0.255
Reactive energy net total | 1.0.128.8.0.255
Apparent energy import total | 1.0.9.8.0.255
Apparent energy export total | 1.0.10.8.0.255
Apparent energy net total | 1.0.137.8.0.255
Active energy import total CO2 | 1.0.1.8.200.255
Active energy import total Currency | 1.0.1.8.220.255
ENERGIES PER TARIFF:
Active energy import tariff 1 | 1.0.1.8.1.255
Active energy import tariff 2 | 1.0.1.8.2.255
Active energy import tariff 3 | 1.0.1.8.3.255
Active energy import tariff 4 | 1.0.1.8.4.255
Active energy import tariff 5 | 1.0.1.8.5.255
Active energy import tariff 6 | 1.0.1.8.6.255
Active energy export tariff 1 | 1.0.2.8.1.255
Active energy export tariff 2 | 1.0.2.8.2.255
Active energy export tariff 3 | 1.0.2.8.3.255
Active energy export tariff 4 | 1.0.2.8.4.255
Active energy export tariff 5 | 1.0.2.8.5.255
Active energy export tariff 6 | 1.0.2.8.6.255
Reactive energy import tariff 1 | 1.0.3.8.1.255
Reactive energy import tariff 2 | 1.0.3.8.2.255
Reactive energy import tariff 3 | 1.0.3.8.3.255
Reactive energy import tariff 4 | 1.0.3.8.4.255
Reactive energy import tariff 5 | 1.0.3.8.5.255
Reactive energy import tariff 6 | 1.0.3.8.6.255
Reactive energy export tariff 1 | 1.0.4.8.1.255
Reactive energy export tariff 2 | 1.0.4.8.2.255
Reactive energy export tariff 3 | 1.0.4.8.3.255
Reactive energy export tariff 4 | 1.0.4.8.4.255
Reactive energy export tariff 5 | 1.0.4.8.5.255
Reactive energy export tariff 6 | 1.0.4.8.6.255
ENERGIES PER PHASE:
Active energy import L1 | 1.0.21.8.0.255
Active energy import L2 | 1.0.41.8.0.255
Active energy import L3 | 1.0.61.8.0.255
Active energy export L1 | 1.0.22.8.0.255
Active energy export L2 | 1.0.42.8.0.255
Active energy export L3 | 1.0.62.8.0.255
Active energy net L1 | 1.0.36.8.0.255
Active energy net L2 | 1.0.56.8.0.255
Active energy net L3 | 1.0.76.8.0.255
Reactive energy import L1 | 1.0.23.8.0.255
Reactive energy import L2 | 1.0.43.8.0.255
Reactive energy import L3 | 1.0.63.8.0.255
Reactive energy export L1 | 1.0.24.8.0.255
Reactive energy export L2 | 1.0.44.8.0.255
Reactive energy export L3 | 1.0.64.8.0.255
Reactive energy net L1 | 1.0.129.8.0.255
Reactive energy net L2 | 1.0.130.8.0.255
Reactive energy net L3 | 1.0.131.8.0.255
Apparent energy import L1 | 1.0.29.8.0.255
Apparent energy import L2 | 1.0.49.8.0.255
Apparent energy import L3 | 1.0.69.8.0.255
Apparent energy export L1 | 1.0.30.8.0.255
Apparent energy export L2 | 1.0.50.8.0.255
Apparent energy export L3 | 1.0.70.8.0.255
Apparent energy net L1 | 1.0.138.8.0.255
Apparent energy net L2 | 1.0.139.8.0.255
Apparent energy net L3 | 1.0.140.8.0.255
INPUTS:
Input 1 counter | 1.128.82.8.0.255
Input 2 counter | 1.129.82.8.0.255
Input 3 counter | 1.130.82.8.0.255
Input 4 counter | 1.131.82.8.0.255
Input 5 counter | 1.132.82.8.0.255
Input 6 counter | 1.133.82.8.0.255
LOAD PROFILE: AVERAGE OF INSTRUMENTATION VALUE
Voltage L1 | 1.0.32.27.0.255
Voltage L2 | 1.0.52.27.0.255
Voltage L3 | 1.0.72.27.0.255
Voltage L1-L2 | 1.0.134.27.0.255
Voltage L2-L3 | 1.0.135.27.0.255
Voltage L1-L3 | 1.0.136.27.0.255
Current L1 | 1.0.31.27.0.255
Current L2 | 1.0.51.27.0.255
Current L3 | 1.0.71.27.0.255
Current N | 1.0.91.27.0.255
THD Voltage L1 | 1.0.32.27.124.255
THD Voltage L2 | 1.0.52.27.124.255
THD Voltage L3 | 1.0.72.27.124.255
THD Voltage L1-L2 | 1.0.134.27.124.255
THD Voltage L2-L3 | 1.0.135.27.124.255
THD Voltage L1-L3 | 1.0.136.27.124.255
THD Current L1 | 1.0.31.27.124.255
THD Current L2 | 1.0.51.27.124.255
THD Current L3 | 1.0.71.27.124.255
THD Current N | 1.0.91.27.124.255
Active power import total | 1.0.16.27.0.255
Active power export total | 1.0.17.27.0.255
Reactive power import total | 1.0.128.27.0.255
Reactive power export total | 1.0.228.27.0.255
Apparent power import total | 1.0.137.27.0.255
Apparent power export total | 1.0.237.27.0.255
Active power import L1 | 1.0.36.27.0.255
Active power import L2 | 1.0.56.27.0.255
Active power import L3 | 1.0.76.27.0.255
Active power export L1 | 1.0.37.27.0.255
Active power export L2 | 1.0.57.27.0.255
Active power export L3 | 1.0.77.27.0.255
Reactive power import L1 | 1.0.129.27.0.255
Reactive power import L2 | 1.0.130.27.0.255
Reactive power import L3 | 1.0.131.27.0.255
Reactive power export L1 | 1.0.229.27.0.255
Reactive power export L2 | 1.0.230.27.0.255
Reactive power export L3 | 1.0.231.27.0.255
Apparent power import L1 | 1.0.138.27.0.255
Apparent power import L2 | 1.0.139.27.0.255
Apparent power import L3 | 1.0.140.27.0.255
Apparent power export L1 | 1.0.238.27.0.255
Apparent power export L2 | 1.0.239.27.0.255
Apparent power export L3 | 1.0.240.7.0.255
Power factor total | 1.0.13.27.0.255
Power factor L1 | 1.0.33.27.0.255
Power factor L2 | 1.0.53.27.0.255
Power factor L3 | 1.0.73.27.0.255
DEMAND MIN/MAX OF INSTRUMENTATION VALUES AND POWERS |  |  |  | Value of X | Meaning
Voltage L1 | 1.0.32.X.0.255 |  |  | 3 | Minimum value of averages calculated over measurement period
Voltage L2 | 1.0.52.X.0.255 |  |  | 6 | Maximum value of averages calculated over measurement period
Voltage L3 | 1.0.72.X.0.255 |  |  | 13 | Minimum sliding value of averages calculated over measurement period
Voltage L1-L2 | 1.0.134.X.0.255 |  |  | 16 | Maximum sliding value of averages calculated over measurement period
Voltage L2-L3 | 1.0.135.X.0.255
Voltage L1-L3 | 1.0.136.X.0.255
Current L1 | 1.0.31.X.0.255
Current L2 | 1.0.51.X.0.255
Current L3 | 1.0.71.X.0.255
Current N | 1.0.91.X.0.255
THD Voltage L1 | 1.0.32.X.124.254
THD Voltage L2 | 1.0.52.X.124.254
THD Voltage L3 | 1.0.72.X.124.254
THD Voltage L1-L2 | 1.0.134.X.124.254
THD Voltage L2-L3 | 1.0.135.X.124.254
THD Voltage L1-L3 | 1.0.136.X.124.254
THD Current L1 | 1.0.31.X.124.254
THD Current L2 | 1.0.51.X.124.254
THD Current L3 | 1.0.71.X.124.254
THD Current N | 1.0.91.X.124.254
Active power import total | 1.0.1.X.0.255
Active power export total | 1.0.2.X.0.255
Reactive power import total | 1.0.3.X.0.255
Reactive power export total | 1.0.4.X.0.255
Apparent power import total | 1.0.9.X.0.255
Apparent power export total | 1.0.10.X.0.255
Active power import L1 | 1.0.21.X.0.255
Active power import L2 | 1.0.41.X.0.255
Active power import L3 | 1.0.61.X.0.255
Active power export L1 | 1.0.22.X.0.255
Active power export L2 | 1.0.42.X.0.255
Active power export L3 | 1.0.62.X.0.255
Reactive power import L1 | 1.0.23.X.0.255
Reactive power import L2 | 1.0.43.X.0.255
Reactive power import L3 | 1.0.63.X.0.255
Reactive power export L1 | 1.0.24.X.0.255
Reactive power export L2 | 1.0.44.X.0.255
Reactive power export L3 | 1.0.64.X.0.255
Apparent power import L1 | 1.0.29.X.0.255
Apparent power import L2 | 1.0.49.X.0.255
Apparent power import L3 | 1.0.69.X.0.255
Apparent power export L1 | 1.0.30.X.0.255
Apparent power export L2 | 1.0.50.X.0.255
Apparent power export L3 | 1.0.70.X.0.255
QUANTITY IDENTIFIERS MONITORED BY ALARMS: |  | Alarm threshold range | Scaler (from FW version 1.4.x)
Voltage L1 | 1.0.32.7.0.255 | 0-999000 | 0.1
Voltage L2 | 1.0.52.7.0.255 | 0-999000 | 0.1
Voltage L3 | 1.0.72.7.0.255 | 0-999000 | 0.1
Voltage L1-L2 | 1.0.134.7.0.255 | 0-999000 | 0.1
Voltage L2-L3 | 1.0.135.7.0.255 | 0-999000 | 0.1
Voltage L1-L3 | 1.0.136.7.0.255 | 0-999000 | 0.1
Current L1 | 1.0.31.7.0.255 | 0-999000 | 0.01
Current L2 | 1.0.51.7.0.255 | 0-999000 | 0.01
Current L3 | 1.0.71.7.0.255 | 0-999000 | 0.01
Current N | 1.0.91.7.0.255 | 0-999000 | 0.01
Current total | 1.0.21.7.0.255 | 0-999000 | 0.01
Active power total | 1.0.16.7.0.255 | 0-999000 | 1
Active power L1 | 1.0.36.7.0.255 | 0-999000 | 1
Active power L2 | 1.0.56.7.0.255 | 0-999000 | 1
Active power L3 | 1.0.76.7.0.255 | 0-999000 | 1
Rective power total | 1.0.128.7.0.255 | 0-999000 | 1
Rective power L1 | 1.0.129.7.0.255 | 0-999000 | 1
Rective power L2 | 1.0.130.7.0.255 | 0-999000 | 1
Rective power L3 | 1.0.131.7.0.255 | 0-999000 | 1
Apparent power total | 1.0.137.7.0.255 | 0-999000 | 1
Apparent power L1 | 1.0.138.7.0.255 | 0-999000 | 1
Apparent power L2 | 1.0.139.7.0.255 | 0-999000 | 1
Apparent power L3 | 1.0.140.7.0.255 | 0-999000 | 1
Power factor total | 1.0.13.7.0.255 | 0-0,99 | 0.001
Power factor L1 | 1.0.33.7.0.255 | 0-0,99 | 0.001
Power factor L2 | 1.0.53.7.0.255 | 0-0,99 | 0.001
Power factor L3 | 1.0.73.7.0.255 | 0-0,99 | 0.001
THD voltage L1 | 1.0.32.7.124.255 | 0-99,9 | 0.1
THD voltage L2 | 1.0.52.7.124.255 | 0-99,9 | 0.1
THD voltage L3 | 1.0.72.7.124.255 | 0-99,9 | 0.1
THD voltage L1-L2 | 1.0.134.7.124.255 | 0-99,9 | 0.1
THD voltage L2-L3 | 1.0.135.7.124.255 | 0-99,9 | 0.1
THD voltage L1-L3 | 1.0.136.7.124.255 | 0-99,9 | 0.1
THD current L1 | 1.0.31.7.124.255 | 0-99,9 | 0.1
THD current L2 | 1.0.51.7.124.255 | 0-99,9 | 0.1
THD current L3 | 1.0.71.7.124.255 | 0-99,9 | 0.1
THD current N | 1.0.91.7.124.255 | 0-99,9 | 0.1
Unbalances phase voltage | 1.0.98.10.10.255 | 0-99,9 | 0.001
Unbalances line voltage | 1.0.98.10.11.255 | 0-99,9 | 0.001
Unbalances current | 1.0.98.10.12.255 | 0-99,9 | 0.001
Frequency | 1.0.14.7.0.255 | 0-999000 | 0.01
Countdown timer | 1.0.0.133.1.255 | 0-999000 | 1

## Event ID
Event ID for notifications (Errors, Alarms and Warnings)
Error Code | Description
40 | Audit log full
41 | Fw CRC error
42 | Error in the data storage area
43 | RAM Mem error (Richiesta IMQ per conformità MID, solo Wave 2 fw)
51 | Hardware problem with analog circuit
52 | hardware problem with analog circuit
53 | hardware problem with RTC
Warning Code | Description
1000 | U1 missing
1001 | U2 missing (and it is not single phase system)
1002 | U3 missing (and it is not single phase system)
1004 | Power on line 1 < 0
1005 | Power on line 2 < 0
1006 | Power on line 3 < 0
1007 | Total power < 0
1008 | Frequency out of the metering limit
1010 | Date not set
1011 | Time not set
1012 | U2 connected for single phase wires setup
1013 | U3 connected for single phase wires setup
1014 | I1 missing
1015 | I2 missing (and it is not single phase system)
1016 | I3 missing (and it is not single phase system)
1017 | I2 connected for single phase wires setup
1018 | I3 connected for single phase wires setup
1019 | IN missing for 4 wires connection
1020 | IN connected in non 4 wires connection
1021 | phase 1 connected to neutral
1022 | phase 2 connected to neutral
1023 | phase 3 connected to neutral
1024 | pulse 1 merged (two high frequency or pulse length for measured power)
1025 | pulse 2 merged (two high frequency or pulse length for measured power)
1026 | pulse 3 merged (two high frequency or pulse length for measured power)
1027 | pulse 4 merged (two high frequency or pulse length for measured power)
1028 | pulse 5 merged (two high frequency or pulse length for measured power)
1029 | pulse 6 merged (two high frequency or pulse length for measured power)
Alarm Code | Description
2013 | Notification of simple alarm 1
2014 | Notification of simple alarm 2
2015 | Notification of simple alarm 3
2016 | Notification of simple alarm 4
2017 | Notification of simple alarm 5
2018 | Notification of simple alarm 6
2019 | Notification of simple alarm 7
2020 | Notification of simple alarm 8
2021 | Notification of simple alarm 9
2022 | Notification of simple alarm 10
2023 | Notification of simple alarm 11
2024 | Notification of simple alarm 12
2025 | Notification of simple alarm 13
2026 | Notification of simple alarm 14
2027 | Notification of simple alarm 15
2028 | Notification of simple alarm 16
2029 | Notification of simple alarm 17
2030 | Notification of simple alarm 18
2031 | Notification of simple alarm 19
2032 | Notification of simple alarm 20
2033 | Notification of simple alarm 21
2034 | Notification of simple alarm 22
2035 | Notification of simple alarm 23
2036 | Notification of simple alarm 24
2037 | Notification of simple alarm 25
2038 | Notification of complex alarm 1
2039 | Notification of complex alarm 2
2040 | Notification of complex alarm 3
2041 | Notification of complex alarm 4
2042 | Notification of complex alarm 5
2043 | Notification of complex alarm 6

## Changes
Map version | Changes
v. 1.2 | Error fix on net energy (signed)
v. 1.3 | Error fix on OBIS codes
New M2M mapping table (available from FW P1.3.10.0)
New registers for power with scaler 1 (available from FW P1.3.10.0)
v.1.3B | New Product ID (2X, MID)
Column with registers - product ref.
v.1.3C | Detailed the notification registers
Added "Event ID" tab
Added missing OBIS codes
v.1.3D | Added scaler for alarm threshold from FW version 1.4.x
Error fix on "Input status" registers
v.1.3E | Error fix on OBIS codes for Alarms
v.1.3F | Error fix on IO setting registers for Product Type
Error fix on "Input counter" registers
v.1.3G | Fix Warning log headers registers
Update Product Type ID columns for IO related registers

## Details
Product type number ID |  | EPiC Mobile | Ekip Connect | Wires
0 | M4M 20 | X |  |  | M4M 20 (Product type number Ids from 0 to 6)
1 | M4M 20 Modbus | X | X |  | 3Ph/4W/3CT = 1
2 | M4M 20 Ethernet | X | X |  | 3 phase-4 wires network+3CTs
3 | M4M 20 Bacnet | X |  |  | 3Ph/4W/1CT = 2
4 | M4M 20 Profibus | X |  |  | 3 phase-4 wires network+1CTs
5 | M4M 20 I/O | X | X |  | 3Ph/3W/3CT = 3
6 | M4M 20 Rogowski | X | X |  | 3 phase-3 wires network+3CTs
7 | M4M 30 Modbus | X | X |  | 3Ph/3W/2CT = 4
8 | M4M 30 Ethernet | X | X |  | 3 phase-3 wires network+2CTs
9 | M4M 30 Bacnet | X |  |  | 3Ph/3W/1CT = 5
10 | M4M 30 Profibus | X |  |  | 3 phase-3 wires network+1CTs
11 | M4M 30 I/O | X | X |  | 2Ph/3W/2CT = 6
12 | M4M 30 Rogowski | X | X |  | 2 phase-3 wires network+2CTs
13 | M4M 20-M RTU | X | X |  | 1Ph/2W/1CT = 7
14 | M4M 20-M ETH | X | X |  | 1 phase-2 wires network+1CTs
15 | M4M 2X RTU | X | X
16 | M4M 2X RTU PQ1 | X | X |  | M4M 30 (Product type number Ids from 7 to 12)
17 | M4M 2X RTU PQ2 | X | X |  | 3Ph/4W/4CT = 0
18 | M4M 2X RTU RTS | X | X |  | 3 phase-4 wires network+4CTs
19 | M4M 2X RTU PQ1+R | X | X |  | 3Ph/4W/3CT = 1
20 | M4M 2X RTU PQ2+R | X | X |  | 3 phase-4 wires network+3CTs
21 | M4M 2X ETH | X | X |  | 3Ph/4W/1CT = 2
22 | M4M 2X ETH PQ1 | X | X |  | 3 phase-4 wires network+1CTs
23 | M4M 2X ETH PQ2 | X | X |  | 3Ph/3W/3CT = 3
24 | M4M 2X ETH RTS | X | X |  | 3 phase-3 wires network+3CTs
25 | M4M 2X ETH PQ1+R | X | X |  | 3Ph/3W/2CT = 4
26 | M4M 2X ETH PQ2+R | X | X |  | 3 phase-3 wires network+2CTs
27 | M4M 30-M RTU | X | X |  | 3Ph/3W/1CT = 5
28 | M4M 30-M ETH | X | X |  | 3 phase-3 wires network+1CTs
2Ph/3W/2CT = 6
2 phase-3 wires network+2CTs
1Ph/2W/1CT = 7
1 phase-2 wires network+1CTs